## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | Full AHIA Review | 10 | 2700 | PBTR-NA | 7 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/patient-bay-emergency-non-acute-treatment/?fullscreen=true&utm_source=project-link&rev=7 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Non-Acute Treatment provides the space equipment and services for assessment, treatment and observation of patients with non-acute conditions and injuries that require a short episode of care (e.g. less than 24 hours) within the Emergency Unit / Emergency Short Stay Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station/write-up area is required for patient observation. ~ The patient bay may be configured with side walls. Inclusion, height and extent of side walls is to be determined at project level to suit the overall department layout and requirements for patient observation. ~ A handwash basin is to be provided for every 4-6 patient bays. Quantity and location of handwashing basins in relation to the patient bay will be subject to the overall department layout and informed by ensuring reasonable travel distances and ease of access from each patient bay. Close access to dedicated PPE bays shared between patient bays is also required separate to bays for handwashing basins. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Inclusion of a patient monitor is optional, and provision is dependent on clinical services requirements. If provided, the patient monitor may be mounted on the patient’s left or the patient’s right. The location of the patient monitor is to be determined at project level to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the bracket for the patient monitor. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The clear area required on each side of the patient trolley for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project suit operational models and local ICT strategies and policies. Services (power, data and/or AV connection) are to be confirmed to suit selected system. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, underbed storage baskets, etc. for clothes and small bags) is to be considered at project level to ensure an appropriate solution is provided for patient and visitor comfort and convenience. ~ It is recommended that a dedicated power outlet, clearly separate from the medical services panel (MSP), is provided to support patient and visitor use for charging portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ In some spaces, such as patient bays, a level of speech privacy of “confidential” would be recommended to protect sensitive patient information. However, due to clinical services requirements for patient care and observation, these spaces cannot be fully enclosed and therefore cannot achieve this level of speech privacy. The speech privacy rating of “not private” has been noted in relation to the elements of the physical environment that can contribute to speech privacy, however, operational approaches to maintaining confidentiality during discussions with patients and support persons must be considered. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple patient bays and possibly brought to the patient bay as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable. However, patient privacy must also be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessments. Refer to Part D Section 6.4 for more information. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 59
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, to patient monitor if provided
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use to charge portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to bedhead wall, low height for patient bed and mattress
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to ceiling recessed examination light; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | optional; may be provided in PPE bay shared between multiple bays
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1 |  | configuration of patient entertainment system will be dependent on operational models and local ICT strategies and policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | optional; required if patient monitor is provided; with cable and accessory management items as required
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of bed; location to ensure visibility along paths of travel
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; located to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; located to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration of patient entertainment system will be dependent on operational models and local ICT strategies and policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to patient monitor if provided
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | with control to patient handset
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements; may alternatively be provided on a mobile stand to be shared across the unit and brought to the patient bay as required
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | optional; provision and configuration of patient monitoring to be confirmed to suit clinical services requirements; with accessories (sensors, cuffs, cables, etc.) as required
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 3 | 1 | Wall Finish 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | provide if patient bay is configured with side walls
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 2 | 1 | Wall Finish 3 | provide if patient bay is configured with side walls; to be coordinated with adjacent wall protection