## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | Full AHIA Review | 25 | 3000 | PBTR-R | 8 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/patient-bay-emergency-resuscitation/?fullscreen=true&utm_source=project-link&rev=8 | 24 hours | 1 patient;; up to 8 staff | The Patient Bay - Emergency, Resuscitation provides the space, equipment and services for assessment, resuscitation, treatment and observation of patients with critical conditions and injuries within the Emergency Unit. | ~ The requirement for body protection or cardiac protection within the Patient Bay - Emergency, Resuscitation, in accordance with AS/NZS 3003, is to be confirmed at project level based on the medical procedures to be undertaken in the space and the level of protection against electric shock afforded in the medical electrical equipment available for these procedures. ~ Clear area is required to both sides of the patient bed to accommodate an ambulance trolley and the staff and equipment required to assist/complete patient transfers. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used should be confirmed at project level. Ceiling mounted patient lifting tracks may be considered based on local WHS policies. ~ Use of mobile imaging equipment within the resuscitation bay is to be confirmed at project level. Radiation shielding and signage requirements will need to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ Clinical requirements and models of care for paediatric and neonatal patients are to be confirmed at project level. One resuscitation bay may be assigned for use with paediatric and neonatal patients and hold the required equipment (e.g. appropriate resuscitation trolleys and warming equipment) and consumables. Alternatively, equipment and consumables for paediatric and neonatal patients may be stored in a central shared zone to be brought any resuscitation bay as required. ~ Clinical requirements and models of care for trauma services, and their resulting spatial requirements are to be confirmed at project level. ~ The content and configuration of the medical services pendant, including medical gases, power and data, will be dependent on clinical services requirements and medical equipment selection, and is to be confirmed at project level. A medical services panel may be provided in lieu of a medical services pendant, depending on models of care and subject to consultation and confirmation with Emergency Unit clinicians. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to the atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given nitrous oxide is used as a recreational drug. ~ Enclosing the Patient Bay - Emergency, Resuscitation may be considered at project level. Where a bay is enclosed, provision of sliding glazed doors that support observation is advised. ~ Where the Patient Bay - Emergency, Resuscitation is enclosed for use as a negative pressure isolation room, an anteroom and an ensuite will be required. A negative pressure room will also have specific air handling and grille location requirements, and these are to be confirmed at project level to suit local engineering services guidance. Provision of negative pressure isolation resuscitation rooms will be dependent on jurisdictional requirements, clinical services planning, service level and patient profile, and must be confirmed at project level. ~ Direct access from ambulance arrivals or a diagnostic imaging room to a Patient Bay - Emergency, Resuscitation may be provided depending on clinical services requirements and operational models. Provision of an additional point of entry to the resuscitation bay will require coordination with ceiling and wall mounted equipment. ~ Personal protective equipment (PPE) is to be in readily accessible locations between resuscitation bays. Refer to Part D: Infection Prevention and Control for more information. ~ Patient monitoring and display screen requirements (e.g. for viewing patient information, review of medical imaging from portable imaging equipment, use of a emergency decision support tool, etc.) are to be confirmed at project level to suit clinical services requirements and local ICT strategies and policies. ~ Provision of cameras for capturing treatment for use in education, streaming to education spaces and/or to enable remote assistance in small services will be dependent on clinical services requirements (including for virtual models of care) and local ICT strategies and policies. ~ Close access is required to linen bays and blanket warming cabinets. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical services requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 108
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, to medication fridge if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to slave display screen for patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | to patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | to diagnostic set
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 4 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional, to display screen for patient information and diagnostic imaging if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional, to display screen for decision support tool if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 6 | 1 |  | 2 over bench, 4 distributed across the room for medical equipment
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1 |  | to electrical services on pendant
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELPR-034 | PANEL: UPS status indicator, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 4 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | for general room lights; to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | provided in addition to PPE bays shared between resuscitation bays
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | provided in addition to PPE bays shared between resuscitation bays
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-104 | BRACKET: suction bottle, on pendant services head | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-115 | BRACKET: sharps bin, trolley mounted | 1 | 1 |  | to resuscitation trolley
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 2 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 3 |  | optional, to display screen for decision support tool if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 3 |  | optional, to display screen for patient information and diagnostic imaging if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-403 | BRACKET: patient monitor, fixed, ceiling mounted | 1 | 1 |  | to slave display screen for patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-414 | BRACKET: patient monitor, articulated, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-423 | BRACKET: ventilator, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIRT-091 | TRACK: IV, ceiling mounted | 1 | 3 |  | optional, may alternatively be provided as services pendant head mounted or mobile poles; to be coordinated with procedure light and medical services pendant
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 8 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | to resuscitation trolley; size to suit clinical services requirements and operational models for frequency of disposal
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | with removable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITBU-436 | CONTROL PANEL: time and elapsed time, synchronised slave clock | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-135 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | wall mounted item is also acceptable
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | wall mounted item is also acceptable
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 | Pendant 1 - Arm 1 | with holder and cable management items as required
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 3 |  | optional, for decision support tool display; provision and placement dependent on clinical services requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 3 |  | optional, for patient information and diagnostic imaging display; provision and placement dependent on clinical service requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 2 | 3 |  | optional, for education and/or to enable remote assistance in small services; provision, quantity and placement is dependent on clinical services requirements and local ICT strategies and policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to slave display screen for patient monitor; services to be confirmed to suit selected equipment, may be replaced with alternate AV outlet depending on system requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITIN-014 | OUTLET: data, single RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | to patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | optional, to medication fridge if provided; for temperature monitoring BMS connection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | optional, to card reader for drug safe if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to display screen for patient information and diagnostic imaging if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to display screen for decision support tool if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITIN-034 | OUTLET: data, triple RJ45, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITIN-064 | OUTLET: data, HDMI, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | to patient monitor; services to be confirmed to suit selected equipment, may be replaced with alternate AV outlet depending on system requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | to write-up workstation; provision of articulated wall or bench mounted brackets may be considered for ergonomics and to support flexible positioning of workstation for visibility of patient.
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 |  | optional, to drug safe if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-211 | BENCH SUPPORT: bracket | 3 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | LIFX-131 | LIGHT: procedure, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | to be coordinated with ceiling mounted IV track and medical services pendant
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 3 | Pendant 1 - Arm 1 | optional, provision of reticulated nitrous oxide to be confirmed to suit clinical services requirements and operational models
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 3 | Pendant 1 - Arm 1 | optional, required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical services requirements and operational models
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 3 | Pendant 1 - Arm 1 | optional, to scavenge outlet if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMGE-039 | HANGER: IV, for ceiling track | 1 | 3 |  | optional, to ceiling track if provided, may alternatively be provided as services pendant head mounted or mobile poles
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1 |  | as required to suit portable equipment positioning
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-191 | CANNISTER: suction bottle | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-235 | DIAGNOSTIC SET: otoscope and ophthalmoscope, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-291 | DEVICE: pump, infusion, single | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-296 | DEVICE: pump, syringe | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | to resuscitation trolley
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-032 | TROLLEY: resuscitation, paediatric | 1 | 3 |  | optional, may alternatively be provided in a shared area between resuscitation bays or in a dedicated resuscitation bay
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMHA-051 | DEVICE: ventilator, adult | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 3 |  | optional, may be provided in a shared area between resuscitation bays; provision in bay will be dependent on operational models for medication management
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPH-021 | FRIDGE: medication/vaccine, 150L nom, single door, under bench | 1 | 3 |  | optional, may be provided in a shared area between resuscitation bays; provision in bay will be dependent on operational models for medication management
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 | Pendant 1 - Arm 1 | configuration of patient monitoring to be confirmed to suit clinical services requirements; with accessories (sensors, cuffs, cables, etc.) as required; connection required for output to ceiling mounted slave monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1 |  | on ceiling mounted bracket, display feed from patient monitor on services pendant head
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 1 | content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMTR-016.02 | TROLLEY: stainless steel, wire mesh drawers, 490W x 600D x 900H nom, 4 drawers | 4 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMTR-053 | TROLLEY: airway/intubation, 750W x 490D x 900H nom | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMTR-092 | TROLLEY: procedure, 600W x 490D x 900H nom | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 5 | 1 | Wall Finish 2
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLPR-006.06 | WALL PROTECTION: corner guards, to 2100 AFFL | 2 | 1 | Wall Protection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLPR-046.03 | WALL PROTECTION: crash rail, to 900 AFFL | 2 | 1 | Wall Protection