## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
RECP-15 | Reception, 15m2 | Public Areas | Translation and QA Only | 15 | 2700 | RECL-15 | 6 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 2 staff seated | The Reception, 15m2 provides the area and amenities for three staff members to receive and check-in patients / visitors to a unit and direct them to their destination or to an adjacent waiting area. The Reception may also act as an administrative base of the unit, including organising bookings for appointments and directing phone calls to other staff, as well as controlling access. Depending on the function of unit, the Reception may also take payments. | ~ Dependent on location, security glazing or shutters may be required. ~ A recessed area for front access by wheelchair users is typically required. Depending on check in requirements at Reception, a set down area for visual access only may be sufficient. ~ Provision of a hearing augmentation system may be required, particularly where security glazing if provided, and requirements are to be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Adjustable height workstations may be provided in line with WHS policies and access for disabled staff working within the Reception area is to be considered. ~ CCTV monitor, intercom and door release buttons linked to entry points may be required for access control depending on location. ~ A desktop printer and labels printer may be provided as required. Printing, scanning and photocopying facilities may be consolidated with ready access from Reception to suit service requirements. ~ Swipe card access to reception may be provided to suit security requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
RECP-15 | Reception, 15m2 | Public Areas | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
RECP-15 | Reception, 15m2 | Public Areas | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
RECP-15 | Reception, 15m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 3 | 1 | Ceiling Finish 2 | [CLGE-001]
RECP-15 | Reception, 15m2 | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
RECP-15 | Reception, 15m2 | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] flush set ceiling is also acceptable
RECP-15 | Reception, 15m2 | Public Areas | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
RECP-15 | Reception, 15m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] 1 to each workstation for charging portable devices, to be located above desk for easy access; location of outlets to meet local WHS requirements
RECP-15 | Reception, 15m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] to printer
RECP-15 | Reception, 15m2 | Public Areas | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | [ELGP-223] 2 to each workstation; extent of emergency power to be determined based on service requirements; location of outlets to meet local WHS requirements
RECP-15 | Reception, 15m2 | Public Areas | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
RECP-15 | Reception, 15m2 | Public Areas | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 3 |  | [ELBO-003] optional, for lighting control across unit/adjacent areas
RECP-15 | Reception, 15m2 | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 18 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided
RECP-15 | Reception, 15m2 | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
RECP-15 | Reception, 15m2 | Public Areas | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018] 1 to each workstation
RECP-15 | Reception, 15m2 | Public Areas | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 2 | 1 |  | [FQSM-007] 1 to each workstation
RECP-15 | Reception, 15m2 | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
RECP-15 | Reception, 15m2 | Public Areas | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to printer
RECP-15 | Reception, 15m2 | Public Areas | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] 1 to each workstation; location of outlets to meet local WHS requirements
RECP-15 | Reception, 15m2 | Public Areas | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | [ITNE-049] 1 to each workstation
RECP-15 | Reception, 15m2 | Public Areas | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007] dual screens may be provided to suit service requirements
RECP-15 | Reception, 15m2 | Public Areas | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
RECP-15 | Reception, 15m2 | Public Areas | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 1 | 1 |  | [ITSE-006]
RECP-15 | Reception, 15m2 | Public Areas | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional
RECP-15 | Reception, 15m2 | Public Areas | SER | ITSE-298 | BUTTON: door release, remote activation, surface mounted | 1 | 3 |  | [ITSE-025] optional, to external entry and/or unit entry as required
RECP-15 | Reception, 15m2 | Public Areas | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1 |  | [FIJO-051]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JOBE-251 | CAP: cable access | 2 | 1 |  | [FIJO-099]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-135]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 2 | 1 |  | [FIJO-106]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JORS-001 | JOINERY UNIT: reception desk | 1 | 1 |  | [FIJO-182]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JORS-041 | WHITEBOARD: fixed, magnetic, integral to reception desk | 1 | 1 |  | [FIBM-019]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JORS-051 | SECURITY GLAZING: to reception | 3 | 3 |  | [WLPT-014] optional
RECP-15 | Reception, 15m2 | Public Areas | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 3 | 3 |  | [WLPT-015] optional
RECP-15 | Reception, 15m2 | Public Areas | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] optional, for temperature control across unit/adjacent areas
RECP-15 | Reception, 15m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]