## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
RECP-E | Reception - Emergency | Emergency | Full AHIA Review | 20 | 2700 | REC-E | 8 | 31.03.2026 |  | 24 hours | 4 staff seated (with up to 2 additional staff intermittently) | The Reception - Emergency provides the space, equipment and services for receiving patients and visitors and directing them to their destination or to the waiting area of the Emergency Unit. The Reception - Emergency also acts as an administrative base for the unit. | ~ Triage - Emergency, Assessment Counters (TRIAGE-CO) and/or Triage - Emergency, Assessment Rooms (TRIAGE-RM) are to be in close proximity to the Reception - Emergency. ~ Multiple Triage - Emergency, Assessment Counters may be combined with the Reception - Emergency. When these Standard Components are combined, the final overall room configuration should include an egress that takes staff behind the secure line of the Emergency Unit. ~ Clear line of sight to the waiting room is recommended for observation. ~ Provision of a window for visual access from Reception - Emergency to a Triage Room/Counter (when these rooms are collocated) may be considered to ensure staff are not isolated in the front of house area. This window may be fixed or an operable sliding type (e.g. to allow passing of items/documents). ~ Provision of a window for visual access to the ambulance entry area (if collocated) may be considered to support efficient registration of patients arriving by ambulance. ~ While oversight of the patient/visitor entry, ambulance entry and waiting room is desirable, it is not always possible and security cameras and feeds are typically required. Display screens for security CCTV feeds should be located so they are not viewable by the public. Size and quantity of screens is to be determined to suit security requirements. ~ An intercom and door release buttons linked to the external entry doors and main department entry point(s) may be required for access control depending on service requirements. Lockdown alarms and buttons will also be required to suit security protocols and operational models for unit lock down. ~ This Standard Component shows 2 x counters where patients/visitors are standing and 1 x wheelchair accessible counter. Counters may be provided as standing height or seated height, or a mix of both, with at least one counter to provide wheelchair access as per AS1428.1 / NZS 4121. ~ Configuration of the security glazing (size of communication slot, size of pass-through aperture for paperwork, etc.) is to be determined at project level to suit operational models. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) and associated items (microphones, signage, etc.) is to be confirmed at project level, in consultation with accessibility experts, to suit the configuration of the counter and security glazing. ~ Acoustic treatment requirements are to be determined suit patient privacy requirements and reduce potential noise transfer to/from the adjacent waiting area. ~ Provision of height adjustable workstations in lieu of fixed joinery benches may be considered at project level and provision should be in line with local WHS policies. Where height adjustable workstations are provided the location of services and the interaction of the moving workstation surface with the static public facing counter must be carefully considered. ~ The final location of doors is to be determined to suit overall department layout and minimise risk of staff entrapment. At least one door must provide an egress that takes staff behind the secure line of the Emergency Department. The other door may provide direct access to the waiting room. Provision of access control devices (e.g. proximity card readers) is to be finalised to suit security requirements. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for stationery and consumables will be dependent on service requirements, operational models and ICT policies and strategies. This includes considering the facility’s use of electronic medical records (EMR) as well as the need to store any remaining paper forms. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the proximity of the counter to adjacent patient areas. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 62
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to waiting area side
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to treatment areas side
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to room side
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to room side
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
RECP-E | Reception - Emergency | Emergency | FIN | CLBK-012 | BULKHEAD: flush set, acoustic | 1 | 1 | Ceiling Finish 2
RECP-E | Reception - Emergency | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
RECP-E | Reception - Emergency | Emergency | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 3 | to bulkhead
RECP-E | Reception - Emergency | Emergency | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
RECP-E | Reception - Emergency | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | to waiting area; may be located to provide direct access to the waiting area or to a zone behind the main entry doors
RECP-E | Reception - Emergency | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 2 | to department treatment areas
RECP-E | Reception - Emergency | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional, to patient flow display screen if provided
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to workstation on wheels (WOW) for roaming clerk(s)
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to clerk workstation for printer
RECP-E | Reception - Emergency | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 6 | 1 |  | 2 to each reception workstation
RECP-E | Reception - Emergency | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 3 | 1 |  | 1 to each reception workstation for printers
RECP-E | Reception - Emergency | Emergency | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | to general room lighting, 1 to each door
RECP-E | Reception - Emergency | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
RECP-E | Reception - Emergency | Emergency | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | optional, to patient flow display screen if provided
RECP-E | Reception - Emergency | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 12 | 1 | Floor Skirting
RECP-E | Reception - Emergency | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
RECP-E | Reception - Emergency | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | FQGE-226 | DEVICE: electronic funds transfer at point of sale (EFTPOS) | 1 | 1 |  | optional; provision dependent on operational models
RECP-E | Reception - Emergency | Emergency | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | FQSM-081 | PEDESTAL: mobile, 660H nominal, 1 drawer and 1 printer shelf | 3 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
RECP-E | Reception - Emergency | Emergency | FFE | ITBU-470 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall mounted | 1 | 1 |  | type of clock and requirement for connection to the master clock system is to be confirmed at a project level based on clinical services requirements
RECP-E | Reception - Emergency | Emergency | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional, provision dependent on clinical services requirements
RECP-E | Reception - Emergency | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to clock; an additional power outlet may be required if power over ethernet (PoE) is not supported by the clock hardware
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to clerk workstation for printer
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to patient flow display screen if provided
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | SER | ITIN-028 | OUTLET: data, double RJ45, surface mounted | 3 | 1 |  | 1 to each reception workstation for printers
RECP-E | Reception - Emergency | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 4 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-071 | TELEPHONE: handset, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | for roaming clerk(s)
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-311 | PRINTER: desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-316 | PRINTER: labels, small, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 3 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | SER | ITSE-091 | BUTTON: security, perimeter lockdown, wall mounted | 1 | 1 |  | to activate lock down tof external entry doors and/or unit entry doors; requirements to be confirmed at project level based on security protocols and operational policies for unit lockdown
RECP-E | Reception - Emergency | Emergency | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | type and size of screen to be confirmed to suit security requirements
RECP-E | Reception - Emergency | Emergency | SER | ITSE-186 | INTERCOM: audio-visual, slave, wall mounted | 1 | 1 |  | connected to intercom at external entry doors and security observation room
RECP-E | Reception - Emergency | Emergency | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
RECP-E | Reception - Emergency | Emergency | SER | ITSE-298 | BUTTON: door release, remote activation, surface mounted | 3 | 1 |  | 1 to each reception workstation; to open external entry doors and/or unit entry doors
RECP-E | Reception - Emergency | Emergency | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to shelving unit
RECP-E | Reception - Emergency | Emergency | FFE | JORS-001 | JOINERY UNIT: reception desk | 2 | 1 |  | counters may be provided as standing height or seated height, or a mix of both; at least one counter to provide wheelchair access as per AS1428.1 / NZS 4121; joinery configuration may include privacy dividers between reception counters to support acoustic privacy with sensitive conversations, and materiality to be confirmed to balance privacy requirements with waiting room observation
RECP-E | Reception - Emergency | Emergency | FFE | JORS-051 | SECURITY GLAZING: to reception | 1 | 1 |  | between reception counters to support acoustic privacy with sensitive conversations and materiality to be confirmed to balance privacy requirements with waiting room observation
RECP-E | Reception - Emergency | Emergency | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 3 | 1 |  | configuration of communication slot and pass through aperture to be confirmed at project level to suit clinical services requirements and operational models
RECP-E | Reception - Emergency | Emergency | FFE | JOSH-001 | SHELF UNIT: tall, adjustable shelves | 1 | 1 |  | type, extent and configuration of storage for stationery and consumables will be dependent on operational models for EMR and local ICT strategies and policies
RECP-E | Reception - Emergency | Emergency | D+W | WIFX-008.01 | WINDOW: fixed, internal, single glazed, sill at 1050H | 1 | 3 | Internal - Window 1 | optional, may be provided to allow for visual access to ambulance entry, if collocated, to support efficient registration of patients; provision is dependent on overall department planning and operational models
RECP-E | Reception - Emergency | Emergency | D+W | WIOP-008 | WINDOW: operable, sliding, internal, single glazed, sill at 1050H | 1 | 3 | Internal - Window 2 | optional, may be provided to triage assessment room, if collocated, to ensure staff are not isolated in the front of house area; provision is dependent on overall department planning, staffing models and WHS policies
RECP-E | Reception - Emergency | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 3 | 1 | Wall Finish 1
RECP-E | Reception - Emergency | Emergency | FIN | WLPR-006.03 | WALL PROTECTION: corner guards, to 1200 AFFL | 3 | 1 | Wall Protection