## Room Template Data
Reporting Room (REPR) - Room Template Properties and Room Template Data
2025-05-15
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
REPR | Reporting Room | 12 |  | 2 | 15.05.2025 | Up to 24 hours | TRUE |  |  |  | (dependent on unit opening hours) | up to 4 staff | The Reporting Room provides two workspaces with high-performance computers for reviewing of and reporting on patient images from various medical imaging modalities. | ~ The size, quantity and configuration of computer display screens is to be finalised based on reviewing and reporting task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. ~ Display screens shown on desk mounted brackets may be wall mounted. Ensure appropriate in-wall support is provided where display screens are to be wall mounted. Where monitors are wall mounted, interaction with height adjustable desks and distances to services connections must be considered. Flexible monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Emerging technology, and its implications for the space, are to be considered. This may include investigating potential hardware, software and process changes that may, for example, result in the inclusion of additional display screens or CPUs, and the ergonomic, services and construction requirements for accommodating these changes in the future (e.g. supports in the wall for mounting, provision for installing additional services, etc.). ~ A large PACS display screen may be provided to be shared between the two workstations for collaborative image reviewing by teams. Screen sharing capabilities from each workstation would be required to support this. Where this is provided, the room occupancy could be up to 8 staff for limited periods. ~ Type and number of data connections for display screens to be confirmed to suit service and equipment requirements (cat-6 data, HDMI, etc.). ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ It is recommended by RANZCR that the light level of the room is able to be lowered to 20-40 lux. The combination of dimmable general room lighting, dimmable indirect lighting (wall and/or ceiling fixtures), and the use of FF&E items such as back lit monitors and keyboards, as well as any light from external sources (e.g. from corridor through glazing), is to be assessed to ensure the overall quality of light in the room is appropriate. Removal of any potential sources of glare on the computer screens is required to ensure it meets requirements for the performance of reviewing and reporting tasks. Each workstation is to have, to the extent possible, independent control for lighting effecting that workstation. ~ Acoustic wall panels and screens shown are indicative and the acoustic treatment of the room is to be designed to mitigate noise transfer between workstations and from adjacent areas. ~ The heat generated by computer equipment is to be considered when determining the air-conditioning requirements for this room. ~ Depending on the location of the Reporting Room, access control (e.g. via proximity card reader) may be provided to ensure staff only access and inclusion of a fixed duress button that is accessible from both workstations may be required to support staff safety. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for shielding to this room will be determined by the arrangement of the overall department floor plan and proximity of the Reporting Room to any imaging modalities. Radiation shielding requirements are to be assessed and advised by a qualified Radiation Consultant. ~ The need for and extent of emergency power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-05-15
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
REPR | Reporting Room | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional - provision to ensure staff only access, requirement dependent on location of room in relation to public/patient areas
REPR | Reporting Room | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
REPR | Reporting Room | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor, coordinated with adjacent wall protection, to suit mobile equipment and patient trolley movement
REPR | Reporting Room | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | cover to vision panel provided as required to reduce transfer of light from corridor
REPR | Reporting Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | optional
REPR | Reporting Room | FFE | FIHR-026 | HOOK: coat | 2 | 1 |  | optional
REPR | Reporting Room | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | FFE | FIHR-231 | BRACKET: computer display screen, triple, articulated, bench/desk mounted | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1
REPR | Reporting Room | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | optional - one additional chair per workstation for consultation and training
REPR | Reporting Room | FFE | FQSN-287 | CABINET: floor standing, 1800H nominal, tambour unit | 1 | 1 |  | optional - type and size of storage solutions to suit service requirements
REPR | Reporting Room | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | FFE | ITNE-171 | DISPLAY SCREEN: computer | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | optional - large wall mounted display screen for collaborative image reviewing
REPR | Reporting Room | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | FFE | ITNE-241 | RECORDER: dictation | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | FFE | MMGE-151 | LIGHT BOX: x-ray viewer, wall mounted | 1 | 1 |  | optional
REPR | Reporting Room | FFE | FQDW-165.07 | WORKSTATION: straight, adjustable height, electric, 720H nom, 800D x 2200W | 2 | 1
REPR | Reporting Room | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
REPR | Reporting Room | FFE | FQGE-109 | SCREEN: privacy, acoustic, floor standing | 1 | 1 |  | as required to reduce noise transfer between workstations
REPR | Reporting Room | FFE | ITNE-251 | CAMERA: webcam, display screen mounted | 2 | 1 |  | optional
REPR | Reporting Room | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
REPR | Reporting Room | FIN | CLTI-022 | CEILING: drop-in tiles, acoustic, prefinished | 1 | 1 | Ceiling Finish 1
REPR | Reporting Room | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
REPR | Reporting Room | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting | aluminium skirting is also acceptable
REPR | Reporting Room | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
REPR | Reporting Room | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 1 | 1 | Wall Finish 2 | as required to reduce noise transfer between workstations
REPR | Reporting Room | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | optional - to x-ray viewer if provided
REPR | Reporting Room | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
REPR | Reporting Room | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | SER | ELSW-021 | SWITCH: light, dimmer | 3 | 1 |  | 1 to general room lighting, 1 to each workstation to indirect lighting
REPR | Reporting Room | SER | ITCL-101 | ANNUNCIATOR: nurse call | 1 | 1
REPR | Reporting Room | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 2 | 1 |  | optional - 1 to each workstation to connect desktop computers to wall mounted display screen if provided
REPR | Reporting Room | SER | ITIN-171 | DESK BOX: power and data outlets, softwired, surface mounted | 2 | 1 |  | 1 to each workstation, for charging/power to portable devices, number and type of power/AV outlets to be confirmed to suit ICT requirements
REPR | Reporting Room | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | optional - provision dependent on location of room in relation to public/patient areas and local WHS policies
REPR | Reporting Room | SER | LIFX-079 | LIGHT: linear, indirect, wall mounted | 2 | 1 |  | dimmable, 1 to each workstation, to be coordinated with general room lighting to suit reporting task requirements
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
1BR-IC
1BR-BA