## Room Template Data
Reporting Workstation (REPW) - Room Template Properties and Room Template Data
2025-05-15
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
REPW | Reporting Workstation | 6 |  | 2 | 15.05.2025 | Available 24 hours | FALSE |  |  |  |  | 1-2 staff | The Reporting Workstation is a single workspace with a high-performance computer for reviewing of and reporting on patient images from various medical imaging modalities. | ~ This Standard Component is provided as a module that would be multiplied in an open plan arrangement. The number of workstations will be determined at a project level to suit service requirements and staffing profile. Shared elements that are not provided at each workstation, e.g. fixed duress in central location, nurse call annunciators, storage, etc. must be considered when modules are combined. ~ Depending on the overall layout when workstation modules are combined, services may be wall mounted for each individual workstation or soft-wired cable trays may be provided and connected to a central point where power and data are wall mounted or delivered via an umbilical/pole from the ceiling or floor. ~ The size, quantity and configuration of computer display screens is to be finalised based on reviewing and reporting task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. ~ Display screens shown on desk mounted brackets may be wall mounted. Ensure appropriate in-wall support is provided where display screens are to be wall mounted. Where monitors are wall mounted, interaction with height adjustable desks and distances to services connections must be considered. Flexible monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Emerging technology, and its implications for the space, are to be considered. This may include investigating potential hardware, software and process changes that may, for example, result in the inclusion of additional display screens or CPUs, and the ergonomic, services and construction requirements for accommodating these changes in the future (e.g. supports in the wall for mounting, provision for installing additional services, etc.). ~ A large PACS display screen may be provided to be shared between multiple workstations for collaborative image reviewing by teams. Screen sharing capabilities from each workstation would be required to support this. ~ Type and number of data connections for display screens to be confirmed to suit service and equipment requirements (cat-6 data, HDMI, etc.). ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ A modesty panel or an extended acoustic panel to the back of the workstation may be required depending on the layout developed for multiple workstations. ~ It is recommended by RANZCR that the light level of the room is able to be lowered to 20-40 lux. The combination of dimmable general room lighting, dimmable indirect lighting (wall and/or ceiling fixtures), and the use of FF&E items such as back lit monitors and keyboards, as well as any light from external sources (e.g. from corridor through glazing), is to be assessed to ensure the overall quality of light in the room is appropriate. Removal of any potential sources of glare on the computer screens is required to ensure it meets requirements for the performance of reviewing and reporting tasks. Each workstation is to have, to the extent possible, independent control for lighting effecting that workstation. ~ Acoustic wall panels and screens shown are indicative and acoustic treatment of the overall room with multiple workstations is to be considered as a whole when designing to mitigate noise transfer between workstations and from adjacent areas. ~ The heat generated by computer equipment is to be considered when determining the air-conditioning requirements for this room. ~ Storage spaces for staff property and stationery may be allocated separately to be shared between multiple workstations. ~ An annunciator for nurse calls may be located to be shared between multiple workstations depending on overall service requirements. ~ Depending on the location of the room containing Reporting Workstations, access control (e.g. via proximity card reader) may be provided to ensure staff only access and the inclusion of a fixed duress button that is accessible in a central location to all workstations may be required to support staff safety. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for shielding to this room will be determined by the arrangement of the overall department floor plan and proximity of the Reporting Room to imaging modalities. Radiation shielding requirements are to be assessed and advised by a qualified Radiation Consultant. ~ The need for and extent of emergency power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-05-15
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
REPW | Reporting Workstation | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
REPW | Reporting Workstation | FFE | FIHR-231 | BRACKET: computer display screen, triple, articulated, bench/desk mounted | 1 | 1
REPW | Reporting Workstation | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | optional - additional chair for consultation and training
REPW | Reporting Workstation | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
REPW | Reporting Workstation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
REPW | Reporting Workstation | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
REPW | Reporting Workstation | FFE | ITNE-171 | DISPLAY SCREEN: computer | 2 | 1
REPW | Reporting Workstation | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1
REPW | Reporting Workstation | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
REPW | Reporting Workstation | FFE | ITNE-241 | RECORDER: dictation | 1 | 1
REPW | Reporting Workstation | FFE | FQDW-165.07 | WORKSTATION: straight, adjustable height, electric, 720H nom, 800D x 2200W | 1 | 1
REPW | Reporting Workstation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
REPW | Reporting Workstation | FFE | FQGE-109 | SCREEN: privacy, acoustic, floor standing | 2 | 1 |  | as required to reduce noise transfer between workstations
REPW | Reporting Workstation | FFE | ITNE-251 | CAMERA: webcam, display screen mounted | 1 | 1 |  | optional
REPW | Reporting Workstation | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
REPW | Reporting Workstation | FIN | CLTI-022 | CEILING: drop-in tiles, acoustic, prefinished | 1 | 1 | Ceiling Finish 1
REPW | Reporting Workstation | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
REPW | Reporting Workstation | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting | aluminium skirting is also acceptable
REPW | Reporting Workstation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
REPW | Reporting Workstation | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 1 | 1 | Wall Finish 2 | as required to reduce noise transfer between workstations
REPW | Reporting Workstation | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
REPW | Reporting Workstation | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
REPW | Reporting Workstation | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to indirect lighting
REPW | Reporting Workstation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1
REPW | Reporting Workstation | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 1 | 1 |  | optional - to connect desktop computers to wall mounted display screen (shared between multiple workstations) if provided
REPW | Reporting Workstation | SER | ITIN-171 | DESK BOX: power and data outlets, softwired, surface mounted | 1 | 1 |  | for charging/power to portable devices, number and type of power/AV outlets to be confirmed to suit ICT requirements
REPW | Reporting Workstation | SER | LIFX-079 | LIGHT: linear, indirect, wall mounted | 1 | 1 |  | dimmable, to be coordinated with general room lighting to suit reporting task requirements
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
1BR-IC
1BR-BA