## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
SECL | Seclusion Room | 15 |  | 1 patient; 1-2 staff intermittently | 24 Hours | Sound attenuation level high, Acoustic privacy is required. | A Seclusion Room provides for the sole confinement of a distressed or agitated person requiring separation for short periods at any hour of the day or night on an involuntary basis. The Seclusion Room will be observable from the Staff Station. An external outlook is desirable. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a standard nominal thickness of 10.38mm, or equivalent approved. Door and joinery hardware should not provide ligature points. Acoustics: Sound attenuation level high; Acoustic privacy is required Additional Design Considerations: - An internal observation window is required - A second room egress door is required

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
SECL | Seclusion Room | FE | FE-7300 | Camera - CCTV security | 1 | in ceiling dome, vandal resistant |  |  |  | Yes | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FF | FF-1252 | Blind - Venetian integral | 3 | to windows & doors, controls outside room |  |  |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FF | FF-13350 | Mattress - foam | 1 | foam, on floor |  |  |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | S-9060 | GPO: Special: for equipment | 1 | CCTV camera in ceiling |  |  |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | S-5000 | Airconditioning | 1 | vandal proof outlet |  |  |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | S-1087 | Special: reading, vandal proof | 1 | sealed, dimmable |  |  |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | S-6060 | Special: night lights | 1 | high level, dimmable |  |  |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 1010 | Floor finish | 1 |  | Vinyl | Cushioned | Seamless, coved | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 3072 | Wall finish | 1 |  | Vinyl | Cushioned | Wall vinyl full height | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 5010 | Ceiling - Plasterboard | 1 | 3000 mm height | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 9006 | Door - 1100mm | 1 | 1100mm clear opening, lockable from outside; anti-hang door hardware | Solid Core/ Safety glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 9001 | Door - 1100mm | 1 | 500mm clear outward opening, optional, additional; anti-hang door hardware | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 7001 | Windows | 1 | external windows double glazed Grade A safety glass with integral venetians |  |  |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 7045 | Observation | 1 | double glazed with integral venetians; Grade A safety glass | Safety glass | Powdercoat | Internal window | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 7015 | Observation | 1 | double glazed with integral venetians; Grade A safety glass | Safety glass | Clear | Through door/s | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 6010 | Cornice | 1 |  | Plasterboard | Paint | 90mm to match ceiling finish | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No