## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
SHAC | Shower - Accessible | Sanitary Facilities | Translation and QA Only | 4 | 2700 | SHD | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff assisting as required | The Shower - Accessible provides an enclosed, lockable room with an accessible shower, hand washing basin and changing area for use by patients, visitors or staff with disabilities (with or without assistance). | ~ The room layout and all fixtures, furniture and equipment (FF&E) are to comply with AS 1428.1 and NZ 4121. ~ Signage with tactile Braille nominating 'All Gender Accessible Shower' required to room. ~ If the Shower - Accessible is located in a patient care area for use by patients, the nurse call system should be included and emergency release door hardware should be installed to allow staff access in emergency situations. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system. ~ Facilities for hand hygiene and PPE to be available nearby if this room is for patient use. ~ If the Shower - Accessible is to be dedicated for use by staff, access control (e.g. a swipe card reader) may be required if this room is provided in a public area or patient care area. ~ The entrance to the room is to be flush with the adjoining floor for access in commode chairs/wheelchairs or with other assistive devices. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
SHAC | Shower - Accessible | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
SHAC | Shower - Accessible | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SHAC | Shower - Accessible | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
SHAC | Shower - Accessible | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
SHAC | Shower - Accessible | Sanitary Facilities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
SHAC | Shower - Accessible | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] with privacy latch, emergency release required if inward opening door
SHAC | Shower - Accessible | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] IPX4 rating required
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1 |  | [FIDI-049] soap dispenser is also acceptable, to shower
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-033] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FIRT-166 | GRAB RAIL: shower, T-shaped, vertical and horizontal | 1 | 1 |  | [FIRT-045] with bracket for hand held accessible shower mounted on vertical rail
SHAC | Shower - Accessible | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
SHAC | Shower - Accessible | Sanitary Facilities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] to be suitable for bare feet; tiles are also acceptable
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
SHAC | Shower - Accessible | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | HYSH-057 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail, accessible | 1 | 1 |  | [HYTP-045]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1 |  | [HYTP-039]
SHAC | Shower - Accessible | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | 1 to shower head
SHAC | Shower - Accessible | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | 1 to shower head
SHAC | Shower - Accessible | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 3 |  | outside door, placement to ensure visibility along paths of travel; optional, to be provided if room located in a patient treatment area for use by patients
SHAC | Shower - Accessible | Sanitary Facilities | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 3 |  | [ITCL-006] IPX4 rating required; optional, to be provided if room located in a patient treatment area for use by patients
SHAC | Shower - Accessible | Sanitary Facilities | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 3 |  | [ITCL-008] IPX4 rating required; optional, to be provided if room located in a patient treatment area for use by patients
SHAC | Shower - Accessible | Sanitary Facilities | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 3 |  | [ITCL-004] IPX4 rating required; optional, to be provided if room located in a patient treatment area for use by patients
SHAC | Shower - Accessible | Sanitary Facilities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional, may be provided if room is for staff use and located in a public / patient treatment area
SHAC | Shower - Accessible | Sanitary Facilities | FFE | JOSH-401 | SHELF: wall mounted, laminate | 1 | 1 |  | [FIJO-194]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | MMGE-024 | CHAIR: shower | 1 | 1 |  | [MMGE-024] wall mounted fold-down bench seat is also acceptable
SHAC | Shower - Accessible | Sanitary Facilities | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable