## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
AMBTR | Ambulance Triage | 12 |  | Up to 3 | 24 Hours |  | The Ambulance Triage is an area for receipt and assessment of patients arriving in the Unit by ambulance. The Ambulance Triage will be adjacent to the Ambulance entry which should include an Airlock.
SHD | Shower - Accessible, 4m2 | 4 |  | 1 patient; 1-2 staff assisting as required | 24 Hours | Sound attenuation level high, Acoustic privacy is required. | The Shower - Accessible is a room containing a shower for use by people with disabilities, either independently or with nurse assistance. The Room is to comply with AS 1428. Acoustics: Sound attenuation level - high; Acoustic privacy required. Body Protected electrical area Additional Design Considerations: - Access is required for commode chairs/ wheelchairs - The floor must not have a raised hob additional text - The door will require escape hardware to allow staff access in an emergency

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
SHD | Shower - Accessible, 4m2 | Fabrics | 1025 | Floor finish | 1 | Default = vinyl; tiles also acceptable | Vinyl, non slip | Studded | Seamless, coved | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | Fabrics | 2000 | Skirting | 1 | Default = vinyl; tiles for tiled floor | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | Fabrics | 3070 | Wall finish | 1 | to wet areas; Default = vinyl; tiles also acceptable | Vinyl | Prefinished | Wall vinyl full height | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | Fabrics | 5023 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | Fabrics | 8010 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | Fabrics | 8040 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | Fabrics | 9001 | Door - 1100mm | 1 | 910mm clear; Outward opening; privacy latch; emergency release | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FE | FE-40412 | TAP - COLD | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FE | FE-40413 | TAP - HOT | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FE | FE-47400 | Shower - hand-held | 1 |  |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-1002 | Bench seat - fold up/down | 1 | reinforced for up to 150kg weight |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-20650 | Soap / shampoo holder | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-23700 | Towel rail | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-3400 | Coathook | 2 | 1 at 1200H for wheelchair users |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-4800 | Curtain track - shower (90deg) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-5300 | Curtain - shower | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-8450 | Grab rail - Shower | 1 | L shaped, optional |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FF | FF-8450 | Grab rail - Shower | 1 | T bar |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-4033 | Floor waste | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-5019 | Exhaust | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-8000 | Patient/ Staff call | 1 | + indicator button & light, water proof |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-8010 | Staff/ Nurse assist call | 1 | + indicator button & light, water proof |  |  |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No