## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
SHD | Shower - Accessible, 4m2 | 4 | 24 Hours | 1 patient; 1-2 staff assisting as required |  | Sound attenuation level high, Acoustic privacy is required. | The Shower - Accessible is a room containing a shower for use by people with disabilities, either independently or with nurse assistance. The Room is to comply with AS 1428. Additional Design Considerations: Access is required for commode chairs/ wheelchairs. The floor must not have a raised hob additional text. The door will require escape hardware to allow staff access in an emergency.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
SHD | Shower - Accessible, 4m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | Outward opening; privacy latch; emergency release | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FIGE-001 | BENCH SEAT: fixed, fold up/down, wet area, wall mounted | 1 | reinforced for up to 150kg weight | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 at 1200H for wheelchair users | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | L shaped, optional | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | T bar | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FIRT-016 | RAIL: towel | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FIRT-033 | TRACK: curtain, shower | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | Default = vinyl; tiles for tiled floor | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FA | FLVY-005 | FLOOR FINISH: vinyl, seamless, coved, non slip, studded | 1 | tiles also acceptable | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | FQGE-011 | CURTAIN: shower | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
SHD | Shower - Accessible, 4m2 | FFE | HYTP-045 | SHOWER: hand-held, accessible | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
SHD | Shower - Accessible, 4m2 | FFE | HYTP-030 | TAPWARE: cold | 1 |  | No | No | Yes | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FFE | HYTP-032 | TAPWARE: hot | 1 |  | No | No | No | Yes | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light, water proof | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light, water proof | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
SHD | Shower - Accessible, 4m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; Default = vinyl; tiles also acceptable | No | No | No | No | No | No | No | No | No