## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
SPECT-CTCR | SPECT-CT Control Room | 14 | Available 24 hours | Up to 3 staff |  | Acoustic privacy required | Room adjacent to the SPECT-CT Imaging Room with direct visibility to the patient for remote control of equipment, and review of procedure images. Additional Design Considerations: X-Ray shielding as advised by Consultant. Cable ducts from the imaging room and equipment room will be required.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
SPECT-CTCR | SPECT-CT Control Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
SPECT-CTCR | SPECT-CT Control Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
SPECT-CTCR | SPECT-CT Control Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
SPECT-CTCR | SPECT-CT Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
SPECT-CTCR | SPECT-CT Control Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
SPECT-CTCR | SPECT-CT Control Room | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1
SPECT-CTCR | SPECT-CT Control Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass
SPECT-CTCR | SPECT-CT Control Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
SPECT-CTCR | SPECT-CT Control Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
SPECT-CTCR | SPECT-CT Control Room | FFE | DWWD-004 | BLIND: roller | 1 | to observation window for patient privacy
SPECT-CTCR | SPECT-CT Control Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
SPECT-CTCR | SPECT-CT Control Room | FFE | FQSN-031 | CABINET: short, single door, tambour, adj shelves, lockable | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-044 | RACK: lead apron | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1 | optional
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-023 | PRINTER: networked | 1 | on benchtop
SPECT-CTCR | SPECT-CT Control Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 1 | communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1 | communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
SPECT-CTCR | SPECT-CT Control Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 2 | high bench at 900-950mm AFFL optional
SPECT-CTCR | SPECT-CT Control Room | FFE | MMMI-269 | COMPUTER: tower, acquisition, SPECT/CT | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | MMMI-274 | CONSOLE: control, SPECT/CT | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIJO-099 | CAC: cable access cap | 2
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | MMMI-369 | DISPLAY SCREEN: contrast injector | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 2
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-076 | BRACKET: for display screen, triple, desk mounted | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 2
SPECT-CTCR | SPECT-CT Control Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 outlet for display screen, patient monitor slave; one outlet for telephone
SPECT-CTCR | SPECT-CT Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4
SPECT-CTCR | SPECT-CT Control Room | SE | ELBO-001 | BUTTON: emergency stop | 1 | mains power, consult manufacturer for safety and compatibility with equipment.
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-135 | GPO: UPS, single, wall mounted | 5
SPECT-CTCR | SPECT-CT Control Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1 | auto on when modality is in use
SPECT-CTCR | SPECT-CT Control Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-208 | GPO: double, wall mounted | 2 | one for printer
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
SPECT-CTCR | SPECT-CT Control Room | SE | ITSE-028 | INTERCOM: audiovisual, wall mounted | 1 | to screening room bed entry door
SPECT-CTCR | SPECT-CT Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 2