## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | Translation and QA Only | 14 | 2700 |  | 2 | 07.04.2026 |  | 8am to 8pm, daily (dependent on unit operating hours) | up to 3 staff | The SPECT-CT Control room is located adjacent to the SPECT-CT Imaging Room, with direct visibility to the patient, for remote control of equipment with audio and visual contact with the patient via cameras, speakers and microphones. | ~ Each Imaging Room requires a Control Room. ~ Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. ~ Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. ~ Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the SPECT-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Some models of SPECT/CT require three phase power to be supplied. ~ Cable management and the potential for computers to be consolidated into a rack (either within the room or in a dedicated, collocated air conditioned room/cupboard) to be determined at project level. ~ Provision of a height adjustable workstation may be considered depending on local policies and staff accessibility requirements. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to control room side
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to imaging room side
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to control room side
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004] to observation window for patient privacy
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-005] to imaging room
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | [DWGL-005]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | [FIHR-044]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | [FIHR-075]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | [FIHR-070]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIHR-341 | BRACKET: display screen, single, articulated, wall mounted | 1 | 1 |  | [FIHR-066]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FQDW-134.04 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1600W | 1 | 1 |  | [FQDW-054]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 1 | 1 |  | [ITAV-014] communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1 |  | [ITAV-057] communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | [ITNE-068]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | [ITNE-070]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-056]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-342 | SCANNER: desktop, document, upright, desktop | 1 | 1 |  | [FQGE-094]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | [FIJO-031]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 3 |  | [MMMI-369] optional
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | MISP-011 | CONTROL CONSOLE: SPECT-CT, dual display screens, keyboard and mouse, control unit, microphone and speaker, desktop | 1 | 1 |  | [MMMI-274]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | MISP-016 | COMPUTER: SPECT-CT, central processing unit (CPU) | 1 | 1 |  | [MMMI-269]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 3 |  | [MMGE-032] optional
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-161 | GPO: single, UPS, wall mounted | 5 | 1 |  | [ELGP-135]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] to printer
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | [ELGP-223]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | [ELBO-012]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | [ELBO-001] mains power, consult manufacturer for safety and compatibility with equipment.
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016] 1 outlet for display screen, patient monitor slave; one outlet for telephone
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | 1 |  | [ITIN-026]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | [LIFX-002] auto on when modality is in use