## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | Translation and QA Only | 50 | 3000 |  | 2 | 07.04.2026 |  | 8am to 8pm, daily (dependent on unit operating hours) | 1 patient;; up to 3 staff assisting | The SPECT-CT Imaging Room provides the area and facilities for Single Photon Emission Computed Tomography (SPECT) scanning procedures with an adjacent Control Room and Equipment Room. The SPECT-CT Imaging Room will be located with ready access to patient dosing areas. | ~ Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. ~ Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. ~ The SPECT-CT Imaging Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints. Where shielding significantly increases the weight of the doors, automatic doors may be considered. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. ~ Configuration of medical gases is to be confirmed to meet clinical requirements such as the provision of anaesthetic services. ~ Dimmable lights are recommended and are to be placed to avoid glare to patients. ~ Back lit ceiling artwork may be installed for patient comfort. ~ 'X-ray in Use' lights are required outside each entry door. ~ Room temperature and humidity control is required. Temperature requirements for equipment are to be confirmed by the vendor, including requirement for circulated cooling water. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the SPECT-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Some models of SPECT/CT require three phase power to be supplied. ~ Structural assessment is required to ensure the floor will be rigid with no vibration and will accommodate the weight of the SPECT-CT unit. ~ Consideration needs to be given to the clearances of equipment and replacement part delivery routes. ~ Where a service is may be performing minor interventional procedures, a Type A handwashing basin will be required instead of Type B. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | [DWSC-005]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-034] to corridor
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 3 | Internal - Window 1 | [DWOB-009] optional, patient observation by camera may be considered, glazing to be AS1428 compliant safety glass
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014] near door
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | [FIHR-030]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-017 | BIN: sharps, clinical, radioactive, high energy, small | 1 | 1 |  | [FQCW-066]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 1 | 1 |  | [ITCL-012 + FIHR-077]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 1 |  | [ITCL-012 + FIHR-078]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | [FIJO-117]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-136]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1 |  | [MMMI-377]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-051 | INJECTOR: contrast, pedestal, mobile | 1 | 3 |  | [MMMI-100] optional, floor or ceiling mounted to be confirmed
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-001 | IMAGING DEVICE: SPECT-CT | 1 | 1 |  | [MMMI-262]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-009 | CART: collimator, SPECT-CT | 4 | 1 |  | [MMMI-264] required quantity dependent on patient mix
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-021 | SYSTEM CABINET: SPECT-CT | 1 | 1 |  | [MMMI-263]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-023 | BOARD: electrical distribution (EDB), SPECT-CT | 1 | 1 |  | [MMMI-265]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-023 | BOARD: electrical distribution (EDB), SPECT-CT | 1 | 1 |  | [MMMI-272]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-041 | PHANTOM: SPECT-CT | 1 | 1 |  | [MMMI-273]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | [MMBE-042]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-045 | POLE: IV, mobile | 1 | 3 |  | [MMGE-045] optional
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-337 | DEVICE: electrocardiography (ECG), with trolley | 1 | 1 |  | [MMGE-179] procured with SPECT/CT system vendor
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 |  | [MMHA-032]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMTR-094 | TROLLEY: procedure, 900W x 490D x 900H nom | 1 | 1 |  | [MMGE-139]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 7 | 1 | Wall Finish 2 | [WLWA-020]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 3 | [WLWA-007]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | [ELGP-122]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | [MMGE-002]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026] patient services
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGE-051 | POWER SUPPLY UNIT: uninterruptable power supply (UPS) | 1 | 3 |  | [ELGT-007] optional, dependent on vendor requirements
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | [ELGP-109] clock
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123.1]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 5 | 1 |  | [ELGP-223] to walls
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | [ELPR-007]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006] on services panel
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012] number determined by number of doors
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel + indicator button & light
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] on services panel + indicator button & light
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] on wall near SPECT/CT unit
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | LIFX-192 | LIGHT: feature, backlit panels, ceiling mounted | 2 | 1 |  | [LIFX-038]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | [LIFX-002] auto on when modality is in use