## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
SRM-15 | Staff Room, 15m2 | Staff Amenities | Translation and QA Only | 15 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 8 staff intermittently | The Staff Room is a shared facility for staff to use for respite, rest and relaxation during meal breaks, especially where it is difficult for staff to use common facilities particularly at night or due to distance. The room may also be used for small meetings or tutorials and for the storage of staff resources or library materials. Facilities for food and beverage preparation and storage should be provided. | ~ An external outlook is desirable. ~ Staff only access may be required if this room is provided in a public or patient care area. ~ A dishwasher may be provided depending on local operational polices. ~ A side approach to the sink for wheelchair access has been shown; front access may be required depending on local/jurisdictional policies and staff requirements. ~ The use of thermal heat detectors for fire detection is recommended. ~ A portable fire extinguisher and fire blanket must be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 4 | 1 |  | [ELGP-109]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 4 | 1 |  | [ELGP-208]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10/ pendulum P3 or agreed equivalent around sink
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQBS-151 | CHAIR: dining areas | 4 | 1 |  | [FQBS-015]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQBS-351 | LOUNGE: 1 seat | 2 | 1 |  | [FQBS-039]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1 |  | [FQBS-042]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQCA-101 | APPLIANCE: microwave, benchtop, domestic | 1 | 1 |  | [FQCA-067]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQCA-402 | FRIDGE: domestic, 300L nom, single door | 1 | 1 |  | [FQCA-032]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQTA-202 | TABLE: square, 450H, 600L | 1 | 1 |  | [FQTA-075]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQTA-425.01 | TABLE: round, 750H, 900 diameter | 1 | 1 |  | [FQTA-055]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] quantity and type of bins to be based on local waste management policies
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | FSSP-101 | FIRE EXTINGUISHER: blanket | 1 | 1 |  | [FSPV-005]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | FSSP-102 | FIRE EXTINGUISHER: dry chemical | 1 | 1 |  | [FSPV-004] type to be confirmed at project level
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | HYBA-304 | SINK: single bowl, with drainer, accessible | 1 | 1 |  | [HYBA-080]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | [HYGE-003] + [HYTP-029] instant hot/cold water tap to sink; provide grille in joinery for ventilation
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink tapware, 1 to boiling/chilled water unit
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITBU-011]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ITCL-101 | ANNUNCIATOR: nurse call | 1 | 3 |  | [ITCL-001] optional, as required in patient care areas, audible
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] 1 x to television, 1 x to telephone
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | [ITIN-070] to television, may be replaced with data outlet in accordance with ICT policy
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOCU-041 | CUPBOARD: tall, with 1 microwave shelf unit | 1 | 1 |  | [FIJO-163]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-143]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JODW-012 | DRAWER UNIT: under bench, single drawer, slide out 1 bin | 1 | 1 |  | [FIJO-226] inclusion will depend on waste management and local IPC policies
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] external outlook is desirable
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 2 | [WLWA-010]