## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
SSTN-10 | Staff Station, 10m2 | 10 |  | Up to 2 staff | 24 Hours | Sound attenuation level medium, Acoustic privacy is required. | The Staff Station is the administrative base for a Unit in which it is located, and enquiry point for patients and visitors. It provides for the co-ordination of patient care, observation, writing up of clinical notes, entering data into computers and making and receiving telephone calls. The Staff Station may also accommodate a Unit Receptionist/ Clerk. The floor area may vary according to the Health Planning Unit, activity level, number of full and part-time staff, the Operational Model and the building layout. Acoustics: Sound attenuation level - Medium; acoustic privacy required. Special Design Requirements: - Staff Station should have a set down area for disabled access - Lockable full height/ counter height doors may be provided for additional security if required. - If doors are required, access for disabled staff may require consideration

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
SSTN-10 | Staff Station, 10m2 | FE | FE-11400 | Computer - PC & monitor | 2 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FE | FE-54510 | Telephone - handset, standard | 2 |  |  |  |  | No | Yes | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FE | FE-68700 | Xray viewer - 2 screen | 1 | recessed |  |  |  | Yes | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FF | FF-11465 | Keyboard shelf - drop down | 2 | optional |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FF | FF-17255 | Pedestal filing unit - mobile, 660mmH | 2 | under bench, lockable |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FF | FF-17360 | Pinboard - fabric covered | 8 | to upstand of staff station |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FF | FF-2100 | Chair - ergonomic, office | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FF | FF-21250 | Staff station - laminate/ timber | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FF | FF-4230 | Counter top | 1 | resinate or laminate, to staff station |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-9001 | GPO: Double | 4 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-9060 | GPO: Special: for equipment | 1 | X-ray viewer |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-1006 | Voice / Data outlet: double | 2 | 1 outlet on each panel for telephone |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-5070 | Temperature control | 1 | control panel, optional |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-1416 | Light Control Panel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-6200 | Light switches (pelmet) | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-6030 | Special: downlights | 1 | dimmable for night lighting |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-6055 | Special: task light, built in | 4 | under countertop |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-8040 | Annunciator | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-10005 | Duress alarm | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | S-7050 | Gas Alarm Panel | 1 | as required |  |  |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 1000 | Floor finish | 1 | Default = vinyl; carpet also acceptable | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 4010 | Wall protection | 1 | to front of desk, optional | Composite | Prefinished PVC | Combined rail & crash bar at 900 AFFL | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 5007 | Ceiling - Plasterboard | 1 | optional | Plasterboard | Paint | Bulkhead | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 5060 | Ceiling - Acoustic | 1 |  | Acoustic | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 9002 | Door - 910mm | 1 | 910mm clear opening, optional to adjoining Office-Clinical | Solid Core/ Glass | Paint | Single leaf, half glazed | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 9050 | Door - 910mm | 1 | 910mm clear opening, lockable, optional for security | Laminate | Prefinished | Single leaf, counter height | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | Fabrics | 2000 | Skirting | 1 | Default = coved vinyl; vinyl featheredge skirting over carpet | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No