## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
SSTN-10 | Staff Station, 10m2 | 10 | 24 Hours | Up to 2 staff |  | Sound attenuation level medium, Acoustic privacy is required. | The Staff Station is the administrative base for a Unit in which it is located, and enquiry point for patients and visitors. It provides for the co-ordination of patient care, observation, writing up of clinical notes, entering data into computers and making and receiving telephone calls. The Staff Station may also accommodate a Unit Receptionist/ Clerk. The floor area may vary according to the Health Planning Unit, activity level, number of full and part-time staff, the Operational Model and the building layout. Special Design Requirements: Staff Station should have a set down area for disabled access. Lockable full height/ counter height doors may be provided for additional security if required. If doors are required, access for disabled staff may require consideration.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
SSTN-10 | Staff Station, 10m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | optional | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FA | DWGE-001 | DOOR: 910mm c/o, single leaf, laminated, counter height | 1 | lockable, optional for security | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FA | DWGL-002 | DOOR: 910mm c/o, single leaf, half glazed, solid core/glass, paint | 1 | optional to adjoining Office-Clinical Workroom | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | ELBO-003 | CONTROL PANEL: lighting | 1 |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | ELBO-015 | SWITCH: light, single | 2 | to built in task lighting | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | ELGP-106 | GPO: single, special, for equipment | 1 | X-ray viewer | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 4 |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 8 | to upstand of staff station | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | FIJO-179 | JOINERY UNIT: staff station, laminate | 1 | resinate or laminate counter top. to staff station | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | Default = coved vinyl; vinyl featheredge skirting over carpet | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | Default = vinyl; carpet also acceptable | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 2 |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | FQDW-004 | KEYBOARD SHELF: drop down, for workstation | 2 | optional | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | FQSM-009 | PEDESTAL: mobile, filing unit, 660H | 2 | under bench, lockable | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | ITCL-001 | ANNUNCIATOR: nurse call | 1 |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 outlet on each panel for telephone | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 2 |  | Yes | Yes | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2 |  | No | Yes | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 |  | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | LIFX-008 | LIGHT: task light, built in | 4 | under countertop | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | optional | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | SE | MGFP-001 | ALARM PANEL: medical gases | 1 | as required | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | MMGE-152 | VIEWER: X-ray, 2 screen | 1 | recessed | Yes | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FA | WLPR-017 | WALL PROTECTION: rail & crash bar combined, at 900 AFFL, prefinished PVC | 1 | to front of desk, optional | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FFE | WLPT-003 | PARTITION: laminate | 2 | under joinery unit | No | No | No | No | No | No | No | No | No
SSTN-10 | Staff Station, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No