## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 2 workstations;;; | The Staff Station is the operational and administrative base of a unit and enquiry point for patients and visitors. It provides for the co-ordination of patient care, patient observation, write-up of clinical notes, data entry and making/receiving telephone calls. The Staff Station may also accommodate a receptionist/ward clerk. | ~ The number of workspaces and area (m2) requirements will vary depending on the type of department, activity level, number of full and part-time staff, operational models and building layout. ~ One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Clinical Workroom. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication (e.g. if a Clinical Workroom and/or multiple Staff Stations are provided). ~ A set down area may be provided for side access by visitors and patients in wheelchairs. If the Staff Station also serves a reception function, a recessed area for front access by wheelchair users may be required. ~ The room may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security as required in high risk areas. ~ Standing-height workstations may be provided. ~ A desktop printer and labels printer may be provided as required. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. ~ Additional monitors may be required for patient monitoring or security purposes depending on service requirements. ~ Placement and visibility of nurse annunciators in adjacent corridors needs to be considered and coordinated with other ceiling elements such as bulkheads. ~ Any rooms that are accessed from behind the staff station will require additional area for appropriate door circulation clearance. ~ Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | [ITNE-049]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | JOBE-251 | CAP: cable access | 2 | 1 |  | [FIJO-099]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | JORS-021 | JOINERY UNIT: staff station | 1 | 1 |  | [FIJO-178] depth of bench and counter top to be confirmed based on service requirements and must consider ergonomics, staff safety and security, WHS requirements and Australian Standards
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | JORS-042 | WHITEBOARD: fixed, magnetic, integral to staff station | 1 | 1 |  | [FIBM-019] under counter top
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] acoustic ceiling treatments are also acceptable, including bulkheads
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 3 |  | [ELPR-007] optional
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] to task lighting
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 3 |  | [ELBO-003] optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] under bench
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] under counter top
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 3 |  | [MGFP-001] optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1 |  | [ELGP-208] for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 2 | 1 |  | [ELGP-223] location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-171 | GPO: single, UPS, joinery mounted | 1 | 1 |  | [ELGP-130] to printer; UPS to be provided if downtime computer required
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-271 | GPO: double, UPS, joinery mounted | 1 | 1 |  | [ELGP-235] UPS to be provided if downtime computer required, location of outlets to meet local operational/WHS requirements