## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
STAD | Store - Accountable Drugs | Pharmacy | Translation and QA Only | 7.5 | 2700 |  | 4 | 07.04.2026 |  | 24 hours | 1-2 staff intermittently | The Store Accountable Drugs is a strongroom located within the Pharmacy Unit for the storage of accountable (Schedule 8) drugs and medications and provides a secure caged area for assembling orders. | ~ This room is to comply with jurisdictional legislation and public health facility policy, including any special provisions for refrigerated medicines. ~ The strong room should be designed in collaboration with an expert security consultant with assessment of the risks for the particular site. ~ The strong room should be independent of the rest of the building structure with no beams or columns passing through the ceiling, walls or floor. ~ The ceiling walls and floor should be built utilisiing suitable construction methods, e.g. reinforced concrete or steel plate modular forms (the wall thickness shown in this Standard Component is indicative only). ~ A gate door is to be provided for security when the main door is open. The security door should be torch and drill resistant, fitted with an appropriate locking mechanism incorporating duress features and an internal release mechanism in case persons are trapped within. ~ The strongroom will require adequate ventilation and a torch and drill resistant breather tube must be fitted to comply with fire regulations. ~ Security monitoring and detection equipment should be incorporated into the alarm system, to detect any attack on the structure. ~ A telephone should be installed for staff safety | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
STAD | Store - Accountable Drugs | Pharmacy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
STAD | Store - Accountable Drugs | Pharmacy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
STAD | Store - Accountable Drugs | Pharmacy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
STAD | Store - Accountable Drugs | Pharmacy | D+W | DOSP-101 | DOOR: hinged, 1 leaf, 900 clear opening, solid, strong room | 1 | 1 | Internal - Door 3 | [DWGE-003] outer door; access and door release controls to be determined based on security strategy
STAD | Store - Accountable Drugs | Pharmacy | D+W | DOSP-121 | DOOR: hinged, 1 leaf, 900 clear opening, mesh grille, strong room | 1 | 1 | Internal - Door 2 | [DWGE-002] inner door; access and door release controls to be determined based on security strategy
STAD | Store - Accountable Drugs | Pharmacy | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208] extent of emergency power to be determined based on service requirements
STAD | Store - Accountable Drugs | Pharmacy | SER | ELGP-231.01 | GPO: double, emergency power, wall mounted, horizontal | 1 | 3 |  | [ELGP-223] optional, for refrigerator if provided
STAD | Store - Accountable Drugs | Pharmacy | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light
STAD | Store - Accountable Drugs | Pharmacy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
STAD | Store - Accountable Drugs | Pharmacy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STAD | Store - Accountable Drugs | Pharmacy | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
STAD | Store - Accountable Drugs | Pharmacy | FFE | FQDW-131.03 | WORKSTATION: straight, adjustable height, 720H nom, 600D x 1500W | 1 | 1 |  | [FQDW-051]
STAD | Store - Accountable Drugs | Pharmacy | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007]
STAD | Store - Accountable Drugs | Pharmacy | FFE | FQSM-202 | SHELVING UNIT: mobile, adjustable shelves, 400D x 600W x 2100H nominal | 3 | 1 |  | [FQSM-048] type and quantity of storage options to be determined based on service requirements
STAD | Store - Accountable Drugs | Pharmacy | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, temperature monitoring, for refrigerator if provided
STAD | Store - Accountable Drugs | Pharmacy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] may be on wall or desk mounted bracket, an additional screen may be provided depending on project ICT requirements
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 1 |  | [ITNE-003]
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-093]
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 1 |  | [ITSE-012+FIHR-002]
STAD | Store - Accountable Drugs | Pharmacy | SER | ITSE-216 | SENSOR: security, vibration detection, for alarm, wall mounted | 1 | 1 |  | [ITSE-003]
STAD | Store - Accountable Drugs | Pharmacy | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2 | [ITSE-038]
STAD | Store - Accountable Drugs | Pharmacy | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
STAD | Store - Accountable Drugs | Pharmacy | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
STAD | Store - Accountable Drugs | Pharmacy | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008] under wall mounted joinery
STAD | Store - Accountable Drugs | Pharmacy | SER | MEGE-015 | PORT: ventilation, secure room | 2 | 1 |  | [MEGE-015]
STAD | Store - Accountable Drugs | Pharmacy | FFE | MMPH-024 | FRIDGE: medication/vaccine, 1000L nom, double door | 1 | 3 |  | [MMGE-034] optional
STAD | Store - Accountable Drugs | Pharmacy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
STAD | Store - Accountable Drugs | Pharmacy | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023] extent dependent on type and height storage solution