## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
STCL | Store - Cleaner | Logistics / Support Services | Translation and QA Only | 12 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Store - Cleaner is a store provided for the central storage of consumables and bulk containers of cleaning chemicals. Large facilities may provide a separate room for the storage of chemicals depending on quantities, safety requirements and operational policies for centralised storage and decanting of chemicals to units. | ~ Hold open door hardware may be required to allow for easy movement of equipment and trolleys in and out of the room. ~ Type and extent of storage solutions for this room will depend on the departments to be serviced and operational models for cleaning and restocking consumables. ~ Type of storage provided for cleaning chemicals, particularly where the storage of significant quantities of chemicals containing flammable ingredients, to be assessed to meet safety and service requirements. ~ A clean linen trolley, or equivalent, may be provided for storage of clean mop heads that are laundered either onsite or offsite. The size of trolley will vary depending on service model and size of facility. ~ Controlled, staff only access is required. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
STCL | Store - Cleaner | Logistics / Support Services | D+W | AFDPR-007.01 | DOOR PROTECTION: plate, heavy duty, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STCL | Store - Cleaner | Logistics / Support Services | D+W | AFDPR-007.01 | DOOR PROTECTION: plate, heavy duty, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STCL | Store - Cleaner | Logistics / Support Services | D+W | AFDPR-057.04 | DOOR FRAME PROTECTION: full wrap, heavy duty, to 1500H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
STCL | Store - Cleaner | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STCL | Store - Cleaner | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STCL | Store - Cleaner | Logistics / Support Services | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021] lockable or secure staff access; hold open hardware may be required; vision panel may be provided
STCL | Store - Cleaner | Logistics / Support Services | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
STCL | Store - Cleaner | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
STCL | Store - Cleaner | Logistics / Support Services | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 1 |  | [FIHR-029] type and extent of storage solutions will be dependent on service requirements
STCL | Store - Cleaner | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
STCL | Store - Cleaner | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STCL | Store - Cleaner | Logistics / Support Services | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 3 | 1 |  | [FQSN-086] type and extent of storage solutions will be dependent on service requirements
STCL | Store - Cleaner | Logistics / Support Services | FFE | FQSN-258 | CABINET: floor standing, 2100H nominal, single door | 1 | 1 |  | [FQSN-012] lockable
STCL | Store - Cleaner | Logistics / Support Services | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
STCL | Store - Cleaner | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
STCL | Store - Cleaner | Logistics / Support Services | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020] height dependent on movement of trolleys and pallets, crash rails are also acceptable