## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | Translation and QA Only | 14 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | A secure room for the storage and recharging of mobile equipment when not in use. | ~ Clear space is required for parking mobile equipment including IV poles, wheelchairs, patient transfer equipment, trolleys and commode chairs. ~ Hooks may be provided for hanging equipment and rails may be provided to mount equipment whilst recharging. ~ Minimum and maximum shelving heights to suit local WHS and infection control policies, as well as fire safety requirements (e.g. the top of stored products is to be no nearer than 500mm to sprinkler deflectors). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 4 | 3 |  | [FIHR-030] optional, provision dependent on service requirements, to be rated for minimum 10kg per hook if provided
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FFE | FIRT-231 | RAIL: equipment charging, vertical, wall mounted | 2 | 3 |  | [FIRT-012] optional, provision dependent on service requirements
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 3 | 1 |  | [FQSN-082] adjustable shelving; type and quantity of storage options to be determined based on service requirements
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-020] height dependent on type and height of mobile equipment, crash rails are also acceptable
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 13 | 1 |  | [ELGP-208] type, quantity and configuration of outlets dependent on operational and equipment requirements