## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
STRT | Stress Testing | Cardiac Investigations | Translation and QA Only | 20 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff | Room for undertaking patient diagnostic stress testing procedures. | ~ The Stress Testing room should be located close to patient toilet and change rooms. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | [DWPR-005] to change room side
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
STRT | Stress Testing | Cardiac Investigations | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-003] optional, to change room if provided
STRT | Stress Testing | Cardiac Investigations | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
STRT | Stress Testing | Cardiac Investigations | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | [FIDI-021]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-019]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
STRT | Stress Testing | Cardiac Investigations | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
STRT | Stress Testing | Cardiac Investigations | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
STRT | Stress Testing | Cardiac Investigations | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-025]
STRT | Stress Testing | Cardiac Investigations | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-028]
STRT | Stress Testing | Cardiac Investigations | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
STRT | Stress Testing | Cardiac Investigations | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 2 | 1 |  | [FQBS-052]
STRT | Stress Testing | Cardiac Investigations | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
STRT | Stress Testing | Cardiac Investigations | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010] to entry door
STRT | Stress Testing | Cardiac Investigations | FFE | FQSM-056 | PEDESTAL: mobile, 840H nominal, 3 equal wire basket drawers | 2 | 1 |  | [FQSM-003]
STRT | Stress Testing | Cardiac Investigations | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
STRT | Stress Testing | Cardiac Investigations | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005]
STRT | Stress Testing | Cardiac Investigations | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010] refer to BHWS-B (similar)
STRT | Stress Testing | Cardiac Investigations | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
STRT | Stress Testing | Cardiac Investigations | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
STRT | Stress Testing | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
STRT | Stress Testing | Cardiac Investigations | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-071]
STRT | Stress Testing | Cardiac Investigations | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
STRT | Stress Testing | Cardiac Investigations | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-131]
STRT | Stress Testing | Cardiac Investigations | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
STRT | Stress Testing | Cardiac Investigations | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
STRT | Stress Testing | Cardiac Investigations | FFE | MIUS-051 | IMAGING DEVICE: echocardiography | 1 | 1 |  | [MMMI-325]
STRT | Stress Testing | Cardiac Investigations | FFE | MMAH-071 | EXERCISE MACHINE: treadmill | 1 | 1 |  | [MMAH-027]
STRT | Stress Testing | Cardiac Investigations | FFE | MMBE-157 | TROLLEY: patient, examination, echocardiography | 1 | 1 |  | [MMBE-069]
STRT | Stress Testing | Cardiac Investigations | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
STRT | Stress Testing | Cardiac Investigations | FFE | MMGE-337 | DEVICE: electrocardiography (ECG), with trolley | 1 | 1 |  | [MMGE-179]
STRT | Stress Testing | Cardiac Investigations | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | [MMHA-002]
STRT | Stress Testing | Cardiac Investigations | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1 |  | [MMHA-027]
STRT | Stress Testing | Cardiac Investigations | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 3 |  | [MMGE-088] optional, for pharmacological stress testing
STRT | Stress Testing | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
STRT | Stress Testing | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
STRT | Stress Testing | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
STRT | Stress Testing | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
STRT | Stress Testing | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
STRT | Stress Testing | Cardiac Investigations | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
STRT | Stress Testing | Cardiac Investigations | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-025]
STRT | Stress Testing | Cardiac Investigations | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | [ELGP-122]
STRT | Stress Testing | Cardiac Investigations | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
STRT | Stress Testing | Cardiac Investigations | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 3 | Panel 1 | [MGAS-022] optional
STRT | Stress Testing | Cardiac Investigations | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042]
STRT | Stress Testing | Cardiac Investigations | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062]
STRT | Stress Testing | Cardiac Investigations | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 3 | Panel 1 | [MGFP-002] optional
STRT | Stress Testing | Cardiac Investigations | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004]
STRT | Stress Testing | Cardiac Investigations | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | [MMGE-002]
STRT | Stress Testing | Cardiac Investigations | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | [ELGP-223]
STRT | Stress Testing | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006]
STRT | Stress Testing | Cardiac Investigations | SER | ELSW-001 | SWITCH: light | 2 | 3 |  | [ELBO-015] optional, to optional change room
STRT | Stress Testing | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
STRT | Stress Testing | Cardiac Investigations | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel, + indicator button & light
STRT | Stress Testing | Cardiac Investigations | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
STRT | Stress Testing | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 5 | 1 |  | [ITIN-026] 1 outlet for telephone