## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
STSS-20 | Store - Sterile Stock, 20m2 | 20 | 24 hours | Up to 3 intermittently |  | A room with an aseptic environment for storage and holding of sterile stock for use in the Operating Suite or other acute treatment areas. Sterile stock may be stored in wire mesh shelving either static units, single mobile units or compactus. Structural engineering advice must be sought if compactus is to be used (floor load bearing capacity and potential deflection effect on walls, doors, etc). Top Track compactus may also be used. Size and number/type of shelving to be adapted to suit specific project briefing and WHS requirements as per AusHFG HPUs. Add 1m2 per 900w400d2100h shelving unit. Compactus units as per manufacturer specifications. Storage height to be limited to 520mm min below ceiling to meet Fire Sprinkler system requirements within AS2118.1. Light fixtures to be sealed.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
STSS-20 | Store - Sterile Stock, 20m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FA | CLFS-005 | CEILING: plasterboard, flush set, suspended, paint, scrub resistant | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FA | DWGL-011 | DOOR: 950mm c/o, single leaf, observation panel, solid core/glass, paint | 3 | auto release, interlock | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 6 | optional | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FA | DWPR-011 | DOOR PROTECTION: protection plate, to full height | 3 | auto release, interlock between door to corridor and door to operating room | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | SE | ELBO-015 | SWITCH: light, single | 3 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | FIHR-065 | BRACKET: for bench, 450D, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | FIJO-013 | BENCH: 450D, open under, stainless steel | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | FQSM-015 | SHELVING: stainless steel wire mesh, mobile | 6 | compactus top-track system is an optional alternative, to be determined at project level | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | FQSM-042 | SHELVING: stainless steel wire mesh, for sutures, mobile | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | ITBU-021 | SYSTEM: barcode tracking | 1 | optional, depends on inventory control policy, if required | Yes | Yes | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | ITCL-018 | CLOCK: clock system slave, digital | 1 | mount flush with wall | Yes | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 |  | No | Yes | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | optional, to bench or wall mounted | No | Yes | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1 |  | Yes | Yes | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 3 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 2 | wording on light to jurisdictional requirements | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | SE | LIFX-003 | LIGHT: illuminated sign, "Laser in Use" | 2 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FFE | MMGE-138 | TROLLEY: preparation | 4 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FA | WLWA-005 | WALL FINISH: paint, scrub resistant | 1 |  | No | No | No | No | No | No | No | No | No
STSS-20 | Store - Sterile Stock, 20m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1 |  | No | No | No | No | No | No | No | No | No