## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
TRBNL | Tribunal Hearing Room | Mental Health | Full AHIA Review | 30 | 2700 |  | 2 | 31.03.2026 |  | 9am to 5pm, Mon - Fri (may vary depending on service requirements for multipurpose use of room) | up to 12 persons seated;;; | The Tribunal Hearing Room provides the space and amenities to support the functions of the Mental Health Tribunal, including hearings, confidential discussions and/or counselling between the Tribunal members, the treating team, consumer, and their support persons and representatives. Hearings may be conducted in person or via video conference. The room may also be used for Staff handovers, clinical reviews, education, large family meetings and other activities during times when not in use as a Tribunal Hearing Room. | ~ Requirements for Tribunal Hearing Rooms, including audio visual/teleconferencing system requirements, will vary across jurisdictions. Refer to local policies for guidance. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ Natural light and external outlook are desirable. Consider placement of windows and room orientation to suit privacy requirements and location of camera for videoconferencing to avoid glare. ~ Requirement for the provision of an adjacent observation area is to be confirmed based on service requirements and jurisdictional policies. Where provided, an observation window with integral venetians is to be provided. ~ Doors should be selected to support safety, dignity and wellbeing. Selections should be non-institutional in appearance to the extent possible. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Inclusion and size of a vision panel to be confirmed to suit service requirements. Privacy film may be applied to the vision panel as required. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ The Tribunal Hearing Room will require safe and effective access and egress. A second door is required. The location and swing of the secondary egress door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (lounges, chairs, tables, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Mobile duress alarms are assumed to be provided. Fixed duress buttons are to also be included at appropriate locations throughout the room (e.g. nearby to secondary egress door or mounted to the underside of a table). Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ Provision of hearing augmentation may be required depending on audio visual/teleconferencing capabilities and features. Requirements to be confirmed at project level. ~ Furniture selected for the room, such as tables and chairs, should be appropriate for the various activities anticipated to be undertaken in the room as per service requirements. A nearby storage area for furniture may be required to support flexible use of the room. ~ Nearby access to a beverage bay and toilet facilities is recommended. ~ Provision of a room booking system (control panel, service requirements) may be considered at project level to suit service requirements and operational models. ~ A high level of acoustic privacy is required for confidentiality. Acoustic treatments and installation to be considered to meet requirements of the mental health environment, including for robustness. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 41
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to room side
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side as required
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to corridor side as required
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
TRBNL | Tribunal Hearing Room | Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
TRBNL | Tribunal Hearing Room | Mental Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 2
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to AV display screen and CPU
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-226 | GPO: double, in floor box | 2 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to each door
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FIHR-332 | BRACKET: display screen, single, fixed, joinery mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
TRBNL | Tribunal Hearing Room | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 10 | 1 | Floor Skirting
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FQBS-142 | CHAIR: meeting room, stackable | 12 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FQTA-125.04 | TABLE: rectangular, 750H, 1500L x 750W, folding, on casters | 4 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-103 | CONTROL PANEL: AV system, joinery mounted | 1 | 1 |  | may alternatively be provided as a wall mounted or portable item
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-134 | CAMERA: AV system, video conferencing, surface mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-147 | MICROPHONE: AV system, portable | 1 | 1 |  | may alternatively be provided as ceiling recessed item
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | optional
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional; to room booking system if provided
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-028 | OUTLET: data, double RJ45, surface mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 1 | 1 |  | to AV display screen and CPU
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-172 | DESK BOX: power and data outlets, softwired, flush mounted | 1 | 1 |  | integral to 1 folding table as required
TRBNL | Tribunal Hearing Room | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | to suit security and egress requirements
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 2 | 1 |  | lockable
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-125 | CUPBOARD: wall mounted, double door, for audio-visual equipment | 1 | 1 |  | lockable; with ventilation as required to suit AV equipment
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-201 | CUPBOARD: under bench, single door | 2 | 1 |  | lockable
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-225 | CUPBOARD: under bench, double door, for audio-visual equipment | 1 | 1 |  | lockable; with ventilation as required to suit AV equipment
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | WIFX-056.04 | WINDOW: fixed, internal, double glazed, sill at 750H, with integral blind | 1 | 1 | Internal - Window 1 | to observation area as required
TRBNL | Tribunal Hearing Room | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1