## Room Template Data
Triage - Emergency, Assessment Counter (TRIAGE-CO) - Room Template Properties and Room Template Data
2025-08-18
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
TRIAGE-CO | Triage - Emergency, Assessment Counter | 6.5 | TRIAGE-1 | 2 | 18.08.2025 | 24 hours | FALSE |  |  |  |  | 1 patient; 1 visitor; 1 staff | The Triage Assessment Counter - Emergency provides the space and facilities for initial assessment of patients presenting to the Emergency Department. | ~ Multiple Triage Assessment Counters may be arranged together and may be connected to or in close proximity to the Reception - Emergency. When Standard Components are combined, the final overall room configuration should include an egress that takes staff behind the secure line of the Emergency Department. ~ Clear line of sight to the waiting room is recommended for observation when the triage nurse is not seeing a patient. ~ Provision of a window for visual access from Reception - Emergency (when these rooms are collocated) may be considered to ensure staff are not isolated in the front of house area. ~ Direct access is required to a handwash basin. This basin is to be shared between multiple Triage Assessment Counters. Refer to Part D: Infection Prevention and Control for more information. ~ This Standard Component shows a counter where patients would be assessed while standing. Counters may be provided as standing height or seated height, or a mix of both – with at least one counter to provide wheelchair access. Where only one triage counter is provided, the configuration must meet requirements for wheelchair access (AS1428.1 or NZS 4121). ~ Security glazing configuration (size of communication slot, size of pass-through aperture for samples/paperwork, support for use of small diagnostic equipment, etc.) is to be determined at project level to suit clinical service requirements and operational models. ~ Provision of a Hearing Loop and associated items (microphones, signage, etc.) to be determined to suit the configuration of the counter and security glazing. ~ Acoustic treatment to be determined suit patient privacy requirements and potential noise transfer from the adjacent waiting area. Finishes must meet IPC requirements. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Triage journey board/bed flow board should be located nearby to Triage Assessment Counters. ~ Ready access to weighing facilities, including baby weighing, is recommended. ~ Ready access to medications, including refrigerated medications, is required. Depending on model of care, access to a separate refrigerator for icepacks, oral rehydration solutions, etc. may also be required to support waiting room medicine. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical service requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. Bins may be located in an area shared between multiple triage counters. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the proximity of the counter to adjacent patient areas. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-08-18
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | provision of adjustable desk mounted brackets for computer screens may be considered at project level
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | JORS-001 | JOINERY UNIT: reception desk | 1 | 1 |  | counters may be provided as standing height or seated height, or a mix of both; at least one counter to provide wheelchair access as per AS1428.1 or NZS 4121.
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | FQSM-081 | PEDESTAL: mobile, 660H nominal, 1 drawer and 1 printer shelf | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | on pedestal under bench
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | JOBE-251 | CAP: cable access | 2 | 1 |  | 1 to computer workstation; 1 to label printer
TRIAGE-CO | Triage - Emergency, Assessment Counter | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 1 | 1 |  | configuration of communication slot and pass through aperture to be confirmed at project level to suit clinical service requirements and operational models
TRIAGE-CO | Triage - Emergency, Assessment Counter | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
TRIAGE-CO | Triage - Emergency, Assessment Counter | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | FIN | WLPT-031 | SCREEN: privacy divider | 1 | 1 | Wall Finish 2 | as required between triage counters to support private conversations; material to be confirmed to balance privacy requirements with waiting room observation
TRIAGE-CO | Triage - Emergency, Assessment Counter | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
TRIAGE-CO | Triage - Emergency, Assessment Counter | FIN | CLBK-012 | BULKHEAD: flush set, acoustic | 1 | 1 | Ceiling Finish 2
TRIAGE-CO | Triage - Emergency, Assessment Counter | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 3 | to bulkhead
TRIAGE-CO | Triage - Emergency, Assessment Counter | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 1 | 1 |  | to computer workstation
TRIAGE-CO | Triage - Emergency, Assessment Counter | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 2 | 1 |  | to printers
TRIAGE-CO | Triage - Emergency, Assessment Counter | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 1 | 1 |  | to computer workstation
TRIAGE-CO | Triage - Emergency, Assessment Counter | SER | ITIN-028 | OUTLET: data, double RJ45, surface mounted | 1 | 1 |  | to printers
TRIAGE-CO | Triage - Emergency, Assessment Counter | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | to entry for emergency department treatment areas
TRIAGE-CO | Triage - Emergency, Assessment Counter | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | located discreetly
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
Emergency | CONS-ENT-OP
Emergency | PTB-E-ACU
Emergency | PTB-E-ACU-E
Emergency | PTB-E-AMB
Emergency | PTB-E-AMT
Emergency | PTB-E-NAC
Emergency | PTB-E-RES
Emergency | RECP-E
Emergency | SSTN-E
Emergency | TRIAGE-CO
Emergency | TRIAGE-RM