## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | Full AHIA Review | 13 | 2700 | TRIAGE-2 | 3 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/triage-emergency-assessment-room/?fullscreen=true&utm_source=project-link&rev=3 | 24 hours | 1 patient; 1 visitor / support person; 1-2 staff | The Triage - Emergency, Assessment Room provides the space, equipment and services for initial assessment, physical examination and commencement of first aid for patients presenting to the Emergency Unit. | ~ This room should be located adjacent or in close proximity to the Reception - Emergency (RECP-E). ~ Provision of a window for visual access from Reception - Emergency (when these rooms are collocated) may be considered to ensure staff are not isolated in the front of house area. ~ Clear line of sight to the waiting room is recommended for observation when the triage nurse is not with a patient. ~ The extent of glazing provided to the room is to be determined at project level to suit the overall department layout and requirements for waiting room observation. Provision of integral blinds or extension of the privacy curtain track over the internal observation window is to be determined to suit requirements for observation and patient privacy. ~ A Type B handwash basin is shown within this Standard Component but may instead be provided nearby and shared between multiple Triage Assessment Rooms. Removal of the handwash basin is subject to consultation with Emergency Unit and Infection Prevention and Control (IPC) staff. Refer to Part D: Infection Prevention and Control for more information. ~ A patient flow/journey board should be located in a shared area nearby to Triage Assessment Rooms. ~ Ready access to height and weight measurement facilities, including baby weighing, is recommended. ~ Ready access to medications, including refrigerated medications, is required. Depending on model of care, access to a separate refrigerator for icepacks, oral rehydration solutions, etc. may also be required to support waiting room medicine. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Input of electronic medical records (EMR) may be performed on a wall mounted computer workstation, a computer on a desk/bench, or on a wirelessly connected workstation on wheels (WOW). Final configuration is dependent on clinical service requirements, operational models for medical records and local ICT strategies and policies. ~ The patient monitor may be mounted on the patient’s left or the patient’s right. The location of the patient monitor is to be determined at project level to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the bracket for the patient monitor. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The weight capacity of recliners selected must be considered to suit a wide range of patient requirements. The recliner must also have the ability to lay completely flat. ~ The clear area required for the use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical services requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins provided, including sharps bins, will be dependent on clinical services requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple triage rooms and possibly brought to the room as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 78
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to room side
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to waiting area side
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | to waiting area; extent of glazing is to be determined at project level to suit the overall department layout and requirements for waiting room observation
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to wall mounted computer
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient monitor
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | low height, for patient recliner
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 3 | Panel 1 | optional, to ceiling recessed examination light if provided; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | collocated with alcohol-based hand rub
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-297 | BRACKET: combined single screen all-in-one computer, keyboard and mouse, height adjustable, wall mounted | 1 | 1 |  | write-up function may be provided by a wall mounted computer workstation, a desk/bench with computer, or a wirelessly connected workstation on wheels (WOW). Final configuration is dependent on clinical service requirements, operational models for medical records and local ICT strategies and policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | with cable and accessory management items as required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 3 | 1 |  | 1 to door from waiting area, 1 to back of room where unit treatment areas are accessed
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to window facing waiting area; provision of integral blinds in lieu of a privacy curtain may be considered at project level to suit local IPC policies and requirements for observation and patient privacy
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 8 | 1 | Floor Skirting
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | 1 to door from waiting area, 1 to back of room where unit treatment areas are accessed
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to window facing waiting area; provision of integral blinds in lieu of a privacy curtain may be considered at project level to suit local IPC policies and requirements for observation and patient privac
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | with removable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry from treatment areas; location to ensure visibility along paths of travel
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; located to support quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; located to support quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to wall mounted computer
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | write-up function may be provided by a wall mounted computer workstation, a desk/bench with computer, or a wirelessly connected workstation on wheels (WOW). Final configuration is dependent on clinical service requirements, operational models for medical records and local ICT strategies and policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | ITNE-203 | INPUT DEVICE: keyboard and mouse, medical grade, washable | 1 | 1 |  | to wall mounted computer
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | optional; provision dependent on clinical service requirements; light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | selected item to be able to lay flat
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | configuration of patient monitoring to be confirmed to suit clinical services requirements; with accessories (sensors, cuffs, cables, etc.) as required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMTR-062 | TROLLEY: dressing, 600W x 490D x 900H nom | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 1 | extent of glazing is to be determined at project level to suit the overall department layout and requirements for waiting room observation; provision of integral blinds or provision of privacy curtain track is to be determined to suit requirements for waiting room observation and patient privacy
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 6 | 1 | Wall Finish 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 3 | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLPR-006.06 | WALL PROTECTION: corner guards, to 2100 AFFL | 3 | 1 | Wall Finish 4