## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
TRMT | Treatment Room | Ambulatory Care | Translation and QA Only | 14 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff | The Treatment Room provides a controlled environment, privacy and facilities for carrying out consultations, examinations, treatments and minor procedures. |  | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
TRMT | Treatment Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
TRMT | Treatment Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
TRMT | Treatment Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
TRMT | Treatment Room | Ambulatory Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | DWGL-033]
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
TRMT | Treatment Room | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
TRMT | Treatment Room | Ambulatory Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
TRMT | Treatment Room | Ambulatory Care | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1 |  | [FQBS-052]
TRMT | Treatment Room | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
TRMT | Treatment Room | Ambulatory Care | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
TRMT | Treatment Room | Ambulatory Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
TRMT | Treatment Room | Ambulatory Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 3 |  | [FQCW-008] optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
TRMT | Treatment Room | Ambulatory Care | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
TRMT | Treatment Room | Ambulatory Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
TRMT | Treatment Room | Ambulatory Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
TRMT | Treatment Room | Ambulatory Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
TRMT | Treatment Room | Ambulatory Care | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
TRMT | Treatment Room | Ambulatory Care | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
TRMT | Treatment Room | Ambulatory Care | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
TRMT | Treatment Room | Ambulatory Care | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
TRMT | Treatment Room | Ambulatory Care | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
TRMT | Treatment Room | Ambulatory Care | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
TRMT | Treatment Room | Ambulatory Care | FFE | MGFP-061 | ADAPTER: suction | 1 | 1 |  | [MMGE-002]
TRMT | Treatment Room | Ambulatory Care | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | [MMBE-043]
TRMT | Treatment Room | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
TRMT | Treatment Room | Ambulatory Care | FFE | MMGE-233 | DIAGNOSTIC SET: otoscope and ophthalmoscope, wall mounted | 1 | 3 |  | [MMGE-031] optional, may be portable/mobile on stand
TRMT | Treatment Room | Ambulatory Care | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119]
TRMT | Treatment Room | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
TRMT | Treatment Room | Ambulatory Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
TRMT | Treatment Room | Ambulatory Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
TRMT | Treatment Room | Ambulatory Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
TRMT | Treatment Room | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
TRMT | Treatment Room | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
TRMT | Treatment Room | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
TRMT | Treatment Room | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-020]
TRMT | Treatment Room | Ambulatory Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
TRMT | Treatment Room | Ambulatory Care | MSP | ELGP-116 | GPO: single, on services panel | 3 | 1 | Panel 1 | [ELGP-105]
TRMT | Treatment Room | Ambulatory Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1 | [ELGP-122]
TRMT | Treatment Room | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
TRMT | Treatment Room | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
TRMT | Treatment Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
TRMT | Treatment Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
TRMT | Treatment Room | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
TRMT | Treatment Room | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
TRMT | Treatment Room | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
TRMT | Treatment Room | Ambulatory Care | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] indicator button and light
TRMT | Treatment Room | Ambulatory Care | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] indicator button and light
TRMT | Treatment Room | Ambulatory Care | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] low level, for patient trolley
TRMT | Treatment Room | Ambulatory Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
TRMT | Treatment Room | Ambulatory Care | SER | ELGP-106.01 | GPO: single, ceiling mounted, horizontal | 1 | 1 |  | [ELGP-101] to exam light
TRMT | Treatment Room | Ambulatory Care | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
TRMT | Treatment Room | Ambulatory Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006]
TRMT | Treatment Room | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light, 1 x examination light
TRMT | Treatment Room | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] indicator button and light
TRMT | Treatment Room | Ambulatory Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] on services panel, call button on the handset
TRMT | Treatment Room | Ambulatory Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to telephone
TRMT | Treatment Room | Ambulatory Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026]
TRMT | Treatment Room | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
TRMT | Treatment Room | Ambulatory Care | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008] under wall mounted joinery
TRMT | Treatment Room | Ambulatory Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
TRMT | Treatment Room | Ambulatory Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
TRMT | Treatment Room | Ambulatory Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
TRMT | Treatment Room | Ambulatory Care | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door