## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
UTRM | Uptake Room | Nuclear Medicine / PET | Translation and QA Only | 10 | 2700 |  | 1 | 07.04.2026 |  | 8am to 8pm, daily (dependent on unit operating hours) | 1 patient;; 1 staff | The Uptake Room is used to inject patients with a radiopharmaceutical and allow them to rest until 'uptake' has occurred before transfer to the scanning room. Patients need to be relaxed in a warm, quiet and dimmed environment to promote uptake. Uptake duration is typically 45 to 60 minutes. | ~ Visual and audio observation of the patient during this time is typically provided from the Control Room of the PET-CT Imaging Room and intercoms, cameras and display screens are to be provided to support patient observation. ~ Injections of radiopharmaceuticals can be undertaken within the room or from outside the room via an automated dose delivery system, which will be accommodated outside each uptake room with a suitable lead-lined injection port in the wall that will allow the coil to be connected to both the machine and the patient (details should be confirmed with vendor) ~ Radiation shielding is required to the room and is to be in accordance with a radiation shielding consultants advice. This will be based on the type of radiopharmaceutical, the number of patients seen on a daily basis and proximity to other services. | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
UTRM | Uptake Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
UTRM | Uptake Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
UTRM | Uptake Room | Nuclear Medicine / PET | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-005] automated, hold open
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 1 |  | [FIHR-029]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 1 | 1 |  | [ITCL-012 + FIHR-077]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 3 |  | [LIFX-027] optional
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | [MMBE-091] consider bariatric capacity as required
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | MIGE-076 | ACCESS PANEL: penetration, uptake room, pass-through for radioisotope injector | 1 | 3 | Wall Finish 2 | [MMMI-219] optional
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 5 | 1 | Wall Finish 1 | [WLWA-020]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1 | [ELGP-122]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | [ELBO-012] inside and outside room, to be reviewed to suit operational requirements
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment screen, may be replaced with data outlet in accordance with ICT policy
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] handsfree to control room