## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
WAIT-30 | Waiting, 30m2 | Public Areas | Translation and QA Only | 30 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 25 patients / visitors;; | The Waiting, 30m2 provides the space and amenities required for patients, visitors / support persons, and families to wait prior to attending an appointment and/or receiving clinical care in a department. | ~ The size of waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. ~ Waiting areas may be shared between departments. ~ Public amenities including baby change facilities should be located nearby. ~ A range of occupants will need to be accommodated including adults, children, able-bodied persons and people with disabilities. In many instances bariatric capacity will also be required. ~ Consider furniture options including weight rating of all chairs and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. ~ Acoustic treatments may be considered as required to ensure the noise level in the space is comfortable both in the waiting area and adjacent reception areas. ~ Check-in kiosks may be located nearby and services will need to be confirmed based on system requirements. ~ In large waiting areas (e.g. Emergency Department, Main Entry) provision of facilities for phone charging may be considered. ~ Provision of a hearing augmentation system may be required where a built in amplification system is provided, if a TV monitor is installed. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection prevention and control (IPC) policies. ~ An external outlook is desirable. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
WAIT-30 | Waiting, 30m2 | Public Areas | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
WAIT-30 | Waiting, 30m2 | Public Areas | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | [ELGP-109] to display screen
WAIT-30 | Waiting, 30m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001] quantity and location to suit local IPC policies
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FIHR-046 | RACK: magazine/pamphlet, wall mounted | 1 | 3 |  | [FIHR-045] optional
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 2 | 1 |  | [FIHR-006]
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-003] carpet tiles are also acceptable
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQBS-102 | CHAIR: visitor, clinical areas, bariatric | 2 | 1 |  | [FQBS-027] quantity to be confirmed at project level depending on service requirements
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQBS-116 | CHAIR: visitor, waiting areas | 21 | 1 |  | [FQBS-032]
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQGE-002 | ARTWORK: wall mounted | 2 | 3 |  | [FQGE-002] optional
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQTA-201 | TABLE: square, 450H, 500L | 3 | 1 |  | [FQTA-071]
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 2 | 1 |  | [ITBU-011]
WAIT-30 | Waiting, 30m2 | Public Areas | SER | ITIN-076 | OUTLET: MATV, wall mounted | 2 | 1 |  | [ITIN-070] may be replaced with data outlet in accordance with local ICT policy
WAIT-30 | Waiting, 30m2 | Public Areas | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light and external outlook is desirable
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-022] as required to suit loose furniture layout; crash rails are also acceptable
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] height to be coordinated with adjacent wall protection