## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
WAIT-SEC | Waiting - Secure | Mental Health | Full AHIA Review | 6 | 2700 |  | 7 | 31.03.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 persons seated;;; | The Waiting - Secure is an area provided for visitors to a Mental Health Unit to wait in comfort prior to or during visits with consumers. Visitors will alert staff of their arrival to gain entry to the unit. | ~ The Waiting - Secure is to be located with direct access to a counter for reception area or a staff station of the Mental Health Unit. Public amenities should be located nearby to allow for ready access. ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (lounges, chairs, tables, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Where caulking required for finishing between surfaces it is recommended "anti-pick" caulking is used. ~ Security provisions for controlled access to the Mental Health Unit are to be confirmed to suit local jurisdictional policies and operational services requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 26
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
WAIT-SEC | Waiting - Secure | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
WAIT-SEC | Waiting - Secure | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
WAIT-SEC | Waiting - Secure | Mental Health | D+W | DOHI-144.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel, with integral blind | 1 | 1 | Internal - Door 1 | from external corridor
WAIT-SEC | Waiting - Secure | Mental Health | D+W | DOHI-144.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel, with integral blind | 1 | 1 | Internal - Door 2 | to mental health unit; provision of tamper proof, anti-ligature and anti-barricade hardware to be confirmed to suit service requirements
WAIT-SEC | Waiting - Secure | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment display screen and CPU
WAIT-SEC | Waiting - Secure | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
WAIT-SEC | Waiting - Secure | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 3 | 1 | Floor Skirting
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQTA-202 | TABLE: square, 450H, 600L | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | 1 to each intercom
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to patient entertainment display screen and CPU
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 2 | 1 |  | to doors
WAIT-SEC | Waiting - Secure | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
WAIT-SEC | Waiting - Secure | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2
WAIT-SEC | Waiting - Secure | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 2 | 1 | Wall Finish 1