## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
WCAC | Toilet - Accessible | Sanitary Facilities | Translation and QA Only | 6 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 person intermittently;;; | The Toilet - Patient provides an enclosed, lockable room with an accessible toilet and handwashing basin for use by patients, visitors or staff with disabilities (with or without assistance). A baby change table may also be located in this room. | ~ The room layout and all fixtures, furniture and equipment (FF&E) are to comply with AS 1428.1 and NZ 4121. ~ Signage with tactile Braille nominating 'All Gender Accessible Toilet' required to room, including noting if the room is a right-handed or left handed room (depending on layout). ~ If the Toilet - Accessible is located in a patient care area for use by patients, the nurse call system should be included and emergency release door hardware should be installed to allow staff access in emergency situations. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system. ~ If the Toilet - Accessible is to be dedicated for use by staff, access control (e.g. a swipe card reader) may be required if this room is provided in a public area or patient care area. ~ The entrance to the room is to be flush with the adjoining floor for access in commode chairs/wheelchairs or with other assistive devices. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
WCAC | Toilet - Accessible | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
WCAC | Toilet - Accessible | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
WCAC | Toilet - Accessible | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] with privacy latch, emergency release required if inward opening door
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIRT-121 | GRAB RAIL: toilet, straight, horizontal | 1 | 1 |  | [FIRT-007]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 1 |  | [FIRT-006]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIRT-191 | BACK REST: toilet, accessible | 1 | 1 |  | [FIGE-011]
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FQGE-361 | CHANGE TABLE: baby, wall mounted | 1 | 3 |  | [FQBS-035] optional
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | HYBA-146 | BASIN: type C, handwashing, accessible | 1 | 1 |  | [HYBA-005] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | HYTP-003 | FLUSH BUTTON: toilet suite, accessible | 1 | 1 |  | [HYWC-001]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | HYTP-052 | TAPWARE: basin, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-035] selection of basin and tapware to be coordinated to ensure compatibility
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | HYWC-033 | TOILET SUITE: patient, accessible | 1 | 1 |  | [HYWC-001]
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 3 |  | outside door, placement to ensure visibility along paths of travel; optional, to be provided if room located in a patient treatment area for use by patients
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 3 |  | [ITCL-006] optional, to be provided if room located in a patient treatment area for use by patients
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 3 |  | [ITCL-008] optional, to be provided if room located in a patient treatment area for use by patients
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 3 |  | [ITCL-004] optional, to be provided if room located in a patient treatment area for use by patients
WCAC | Toilet - Accessible | Sanitary Facilities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038] optional, may be provided if room is for staff use and located in a public / patient treatment area
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin