## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
WCPT | Toilet - Patient | Sanitary Facilities | Translation and QA Only | 4 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1 staff assisting as required | The Toilet - Patient provides an enclosed, lockable room with a toilet and handwashing basin for use by patients (with or without assistance). | ~ Signage with tactile Braille nominating 'All Gender Patient Toilet' required to room. ~ Emergency release door hardware should be installed to allow staff access in emergency situations. ~ The entrance to the room is to be flush with the adjoining floor for access in commode chairs/wheelchairs or with other assistive devices. ~ Toilet lids and seats are to be robust and suitable for long term, high frequency use. It is recommended that the toilet lid/seat is coloured to achieve a minimum 30% luminance contrast between the lid/seat, and the toilet pan, the floor, and the adjacent walls to support patients with visual impairments. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
WCPT | Toilet - Patient | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
WCPT | Toilet - Patient | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
WCPT | Toilet - Patient | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WCPT | Toilet - Patient | Sanitary Facilities | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
WCPT | Toilet - Patient | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] with privacy latch, emergency release required if inward opening door
WCPT | Toilet - Patient | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 1 | 1 |  | [FIHR-026]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 1 |  | [FIRT-006]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIRT-136 | GRAB RAIL: toilet, drop down | 1 | 3 |  | [FIRT-008] optional
WCPT | Toilet - Patient | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
WCPT | Toilet - Patient | Sanitary Facilities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
WCPT | Toilet - Patient | Sanitary Facilities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
WCPT | Toilet - Patient | Sanitary Facilities | FFE | HYWC-021 | TOILET SUITE: standard | 1 | 1 |  | [HYWC-008]
WCPT | Toilet - Patient | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door; placement to ensure visibility along paths of travel
WCPT | Toilet - Patient | Sanitary Facilities | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006]
WCPT | Toilet - Patient | Sanitary Facilities | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
WCPT | Toilet - Patient | Sanitary Facilities | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
WCPT | Toilet - Patient | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
WCPT | Toilet - Patient | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin