## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
WTPL | Water Treatment Plant Room | 15 |  | 1 - 2 | 24 Hours |  | The Water Treatment Plant Room is a lockable room for water treatment systems used in dialysis, including booster pumps, particle filters, water softeners, carbon filters and reverse osmosis systems. Refer to Manufacturer's Specifications for details of Reverse Osmosis (RO) Water Treatment Plant equipment. In particular this equipment will incorporate a heat disinfection function, and water saving features. The Water Treatment Plant Room should be located in close proximity to the Renal Dialysis Unit to permit short tubing runs to each Treatment Bay, and permit staff to monitor and service the water treatment systems. Special Design Requirements: - Ventilation, exhaust and/or airconditioning must be deisgned to accommodate the heat loads of the specified equipment. - High level sound isolation is required to ensure noise generated from this room does not invade Treatment spaces - Structural Engineer's assessment must be sought for floor load bearing capacity with respect to water treatment and pre- treatment plant equipment - Service access will be required aound the perimeter of all plant equipment - Pipework and components installed after the water inlet within this room shall not contain brass or copper

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Items | [6 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
WTPL | Water Treatment Plant Room | FE | FE-42295 | Pump - pressure booster | 2 | as needed to achieve required water pressure |  |  |  | Yes | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FE | FE-61295 | Water treatment plant equipment | 10 | RO Plant; details according to Manufacturer's Specifications |  |  |  | Yes | No | Yes | No | No | No | Yes | No | No
WTPL | Water Treatment Plant Room | FF | FF-1050 | Bench - laminate | 1 | work bench |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | FF | FF-21680 | Stool - adjustable, mobile | 1 | under bench |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-9011 | GPO: Emergency power, double (H) | 4 | for use of hand tools in the room, on a separate circuit |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-9060 | GPO: Special: for equipment | 1 | 3 phase, according to Manufacturer's specifications |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-9060 | GPO: Special: for equipment | 2 | pumps, as required |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-1002 | Alarm | 1 | to Staff Station - Renal Unit for Plant Equipment status/ malfunction |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-4005 | Cold water | 1 | inlet for RO Water Treatment Plant Equipment |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-4033 | Floor waste | 1 | floor waste must be capable of high flow rates and high temperature water (up to 95 degrees C) from the RO Water Plant |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-5000 | Airconditioning | 1 | A/C & exhaust system to accommodate heat loads generated by plant eqeuipment |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-5019 | Exhaust | 1 | heat extraction will be required |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | Fabrics | 1280 | Floor finish | 1 |  | Concrete | Trowel | Sealed | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | Fabrics | 5021 | Ceiling - Plasterboard | 1 | Min Height 2400mm; Water resistant drop in tile ceiling also acceptable | Plasterboard | Paint, washable | Water resistant, flush set, suspended | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | Fabrics | 9110 | Door - 1400mm | 1 | 1600mm clear opening, lockable | Solid Core | Paint | 1 1/2 leaf | No | No | No | No | No | No | No | No | No
WTPL | Water Treatment Plant Room | Fabrics | 2155 | Skirting | 1 |  | Concrete | Sealed | Coved concrete to 150 AFFL | No | No | No | No | No | No | No | No | No