## SSU Rev 7.0
HPU 190 STERILIZING SERVICES UNIT -SCHEDULE OF ACCOMMODATION, REVISION 7
STERILISING SERVICES UNIT
ENTRY
Room Code | Room / Space | SC / SC-D | FRD Code | 2 Operating Rooms |  | 10 Operating Rooms |  | 20 Operating Rooms |  | Remarks
|  |  |  | Qty | m2 | Qty | m2 | Qty | m2
OFF-1P-9 | Office - Single Person | Yes | SSU01 | 1 | 9 (o) | 1 | 9 | 1 | 9 | Optional for smaller unit depending on staff profile. Total number of workstations will depend on staff profile and local jurisdictional policies. Larger units may require a dedicated reception area in addition to office spaces.
OFF-WS | Office - Workstation | Yes | SSU01 |  | 4.5 |  | 4.5 |  | 4.5 | Number of workstations will be dependent on staff profile and local jurisdictional policies.
| Discounted Circulation |  |  |  | 25% |  | 25% |  | 25%
Reprocessing Areas
Room Code | Room / Space | SC / SC-D | FRD Code | 2 Operating Rooms |  | 10 Operating Rooms |  | 20 Operating Rooms |  | Remarks
|  |  |  | Qty | m2 | Qty | m2 | Qty | m2
Loan RMD Receipt and Dispatch
| Loan Sets Room |  | SSU14 | (o) | 30 | 1 | 50 | 1 | 70 | Optional for smaller units depending on casemix or whether they operate as a hub and spoke or reprocess for external customers, as this room could be used as a receipt and dispatch area for these circumstances. The actual spatial requirements for a Loan Sets room is dependent on facility casemix. Specific casemix requirements should be taken into account with reference to user requirements.
Receiving / Cleaning / Decontamination
| Receiving Area |  | SSU05 | 1 | 40 | 1 | 130 | 1 | 195 | Lobby space will be required in the Operating Unit to accomodate trolleys waiting to be loaded into lifts/hoists. Lobby space will also be required in the SSU to accommodate trolleys that have been unloaded from lifts/hoists but have not yet been formally received into SSU.
| Cleaning (Decontamination) Room |  | SSU06 | [6 empty] | If automated loading of washer-disinfectors is selected, the space requirements of the particular automation system must be taken into account in allocating floor area. Includes storage for cleaning brushes and consumables.
DISP-8 | Disposal room | Yes | SSU07 | 1 | 5 | 1 | 15 | 1 | 20 | Access to Cleaning (Decontamination) room and external corridor. This may be a bay for smaller units. Disposal room is for SSU produced waste only.
CLRM-5 | Cleaner's Room (soiled side) | Yes | SSU08 | 1 | 5 | 1 | 5 | 1 | 5 | Two cleaners rooms are expected for large SSUs. A single room with two separate sets of cleaning equipment is acceptable for small SSUs.
| Washer Disinfectors |  | SSU10 SSU11 | 1 | 10 | 1 | 20 | 1 | 35 | Includes other pass through equipment such as RMD drying cabinets. Check dimensions of preferred supplier's equipment to confirm allowances. Rural and remote health services will require a minimum of 2 WDs.
| Trolley Wash |  | SSU12 |  |  | 1 | 15 | 1 | 30 | Smaller SSUs may manually clean trolleys, check with the user to confirm requirements. Where SSUs service a large volume of external customers, operate as a 'hub and spoke' or handle a large number of loan sets, provision of a trolley washer should be considered.
Room Code | Room / Space | SC / SC-D | FRD Code | 2 Operating Rooms |  | 10 Operating Rooms |  | 20 Operating Rooms |  | Remarks
|  |  |  | Qty | m2 | Qty | m2 | Qty | m2
Inspection, Assembly and Packaging
| Inspection, Assembly and Packaging (IAP) |  | SSU13 | 1 | 45 | 1 | 105 | 1 | 220 | If automated unloading of washer-disinfectors and automated loading of sterilisers is selected, the space requirements of the particular automation system must be taken into account in allocating floor area.
| Sterilizers |  | SSU18 SSU19 | 1 | 8 | 1 | 20 | 1 | 30 | Check dimensions of preferred supplier's sterilizers to confirm allowances. Space allocations will be altered by the selected sterilizer capacity. Rural and remote health services will require a minimum of 2 sterilizers.
STGN | Store - General | Yes | SSU15 | 1 | 15 | 1 | 20 | 1 | 40 | The Consumables Store may be shared with the Operating Unit in smaller SSUs. Consideration needs to be given to proximity to the SSU in this scenario. Discuss with users during planning stages.
CLRM-5 | Cleaner's room (clean side) | Yes | SSU17 | 1 | 5 | 1 | 5 | 1 | 5 | Two cleaners rooms are expected for large SSUs. A single room with two separate sets of cleaning equipment is acceptable for small SSUs
Cooling and Dispatch
| Sterilizer Unloading and Cooling Area |  | SSU20 | 1 | 30 | 1 | 75 | 1 | 190 | If automated unloading of sterilisers is selected, the space requirements of the particular automation system must be taken into account in allocating floor area
| Dispatch - operating unit |  | SSU21 | [6 empty] | Assumes RMDs are returned and stored in the Operating Unit's Sterile Storage Room. Lobby space will be required to accommodate trolleys prepared and waiting for dispatch to the Operating Unit. Lobby space may also be required in the Operating Unit to accommodate trolleys of processed RMDs not yet formally received into the Operating Unit.
| Dispatch - other units |  | SSU22 | [6 empty] | e.g. IPUs, ED and Critical Care Units. Assumes RMD are returned and stored at the point of use. If the facility operates as a hub and spoke or services a large number of external customers, spatial allocations may need to be increased. Confirm with users during planning stages.
| Discounted Circulation |  |  |  | 16% |  | 16% |  | 16%
SUPPORT AREAS
Room Code | Room / Space | SC / SC-D | FRD Code | 2 Operating Rooms |  | 10 Operating Rooms |  | 20 Operating Rooms |  | Remarks
|  |  |  | Qty | m2 | Qty | m2 | Qty | m2
| Store - Chemical Dosing |  | SSU09 | 1 | 2 | 1 | 5 | 1 | 10 | Smaller SSUs may use a chemical storage cupboard. Some suppliers require space for chemical dosing within the Cleaning (Decontamination) Room for central chemical dosing. Confirm requirements with the users.
| Store - Deboxing and Consumables |  | SSU15 | 1 | 10 | 1 | 20 | 1 | 40 | May be shared with the Operating Unit if appropriate. Deboxing must be a separate room, with easy access to the consumable store. The proportion of space allocated to deboxing versus storage should be confirmed with the user.
| ID Station |  | SSU16 | 1 | 2 | 1 | 4 | 1 | 10 | An ID Station is required where the hospital is tracking RMDs at the instrument level to accommodate instrument marking equipment and the staff that use it. Smaller SSUs may use a bay rather than a separate room.
| Plant Room - SSU |  | SSU03 | 1 | 5 | 1 | 40 | 1 | 60 | Includes water treatment plant. This area can be combined with general hospital plant if location is suitable.
| Discounted Circulation |  |  |  | 16% |  | 16% |  | 16%
STAFF AREAS
Room Code | Room / Space | SC / SC-D | FRD Code | 2 Operating Rooms |  | 10 Operating Rooms |  | 20 Operating Rooms |  | Remarks
|  |  |  | Qty | m2 | Qty | m2 | Qty | m2
CHST-10 | Change – Staff | Yes | SSU02 | Shared (see note) |  | 2 | 10 | 2 | 25 | Assumed shared amenities with Operating Unit for 2 Operating Room scenario. Additional spatial allocation will be required if SSU is remote from Operating Unit - otherwise use communal staff amenities where possible. Ensure that the sizing of any shared amenities takes into consideration the additional number of SSU staff that will be using the change rooms, staff room and other amenities such as toilets.
SRM-15 | Staff Room | Yes | SSU02 | Shared (see note) |  | 1 | 15 | 1 | 20
MEET-15 | Meeting Room | Yes | SSU02 | Shared (see note) |  | 1 | 15 | 1 | 15
| Discounted Circulation | [5 empty] | 10% |  | 10%

## ERU Rev 7.0
HPU 190 STERILISING SERVICES UNIT -SCHEDULE OF ACCOMMODATION, REVISION 7
ENDOSCOPE REPROCESSING
Room Code | Room / Space | SC / SC-D | FRD Code | 1-2 Procedure Rooms |  | 4 Procedure Rooms |  | Remarks
|  |  |  | Qty | m2 | Qty | m2
| Endoscope Reprocessing - Dirty |  | SSU23 | 1 | 13 | 1 | 17 | One double basin sink per one-two procedure rooms is assumed. This space may be reduced by 2m2 if consumable or chemical storage can be shared within an integrated SSU.
| Automated Flexible Endoscope Reprocessors (AFERs) |  | SSU24 | 1 | 4 | 1 | 8 | The number of AFERs should provide capacity to process two endoscopes for each procedure room. Some AFERs are able to process two endoscopes at a time or asynchronously. Rural and remote health services will require a minimum of 2 AFERs. Check dimensions of preferred supplier's AFERs to confirm allowances. Note that the Quantity "1" refers to the number of spaces, not the number of AFERs or other equipment
| Endoscope Reprocessing - Clean |  | SSU25 | 1 | 8 | 1 | 14 | This space may be reduced by 2m2 if consumable or chemical storage can be shared within an integrated SSU.
| Endoscope Reprocessing - Storage (CESC or equivalent system) |  | SSU26 | 1 | 4 | 1 | 8 | Fleet size and the number of storage positions required must be confirmed with the user. Note that the Quantity "1" refers to the number of spaces, not the number of storage cabinets or storage positions. Where a storage bag system is used instead of CESCs, space will be required for the storage of the bagged endoscopes.
| Store - Chemicals |  | SSU27 | 1 | 2 | 1 | 4 | Area allocation will depend on the volume of chemicals required to service the projected workload. Some reprocessing agents used for endoscopy reprocessing are flammable and/or toxic. Storage of these agents will comply with jurisdictional workplace health and safety regulations. This space may need to be ventilated to exhaust air to a safe location outside the building.
| Discounted Circulation |  |  |  | 16% |  | 16% | Personnel access should be provided between the clean and dirty sections of the ERU without transit through the procedure room.