## ED SOA Rev 8
HPU 300 Emergency Unit - Schedule of Accommodation, Revision 8
ENTRY / PUBLIC AMENITIES
Room Code | Room Name | SC/ SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock - Entry | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 3 | 3 | Allocation dependent on nearby amenities. Toilet numbers provided are indicative only and must comply with the recommendations of building surveyors in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Accessible Changing Facility |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Toilet facilities for people with high support needs may be provided if not provided elsewhere (refer to 'Changing Places' information for Australian facilities). Larger area will be required if shower is to be provided. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for min 2 staff, 20m2 for min 3 staff & 30m2 for min 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 (o) | 1 | 1 (o) | Optional. Separate fridge (with optional freezer) for medications and drinks e.g. hydration fluids shared by all Triage spaces to support waiting room medicine. Provide if local jurisdictional policies for medication storage allows its provision.
BHW | Bay - Height / Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 1 | 7 | 1 | 10 | Wheelchair/trolley hold.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non-public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry.
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. Final spaces dependent on write-up spaces required and peak number of ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | Shared |  | 1 | 4
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
Room Code | Room Name | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 5 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning. Consider visual and acoustic privacy for children if paediatric resuscitation bay is collocated. May be enclosed if there is a requirement for humidity control and containment.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [7 empty] | 30 (o) | Optional. Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTV | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
Room Code | Room Name | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 | Dedicated to each Class N Room.
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 2 | 5 | 3 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Adjacent to allocated bariatric bay.
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Optional. Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Optional. Attached to the Consult Room - Sexual Assault
PROC | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Optional. Included under paediatric zone below for smaller services.
INTV | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 | Optional for 6-bay scenario depending on location of nearby patient amenities. Final number in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-10 SSTN-14 SSTN-20 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30 | 60-bed scenario may provide 2 x 15m2 Staff Stations instead.
| Staff Station, Emergency Control | [6 empty] | 14 (o) TBC | 1 | 14 (o) TBC | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 14 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. May be a combined room in 60-bed scenario.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design.
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube Station | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1 | Consider additional BPTS in Resuscitation Area if location cannot be centralised.
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and Ambulatory Care zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and Ambulatory Care zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
PAEDIATRIC ZONE
Room Code | Room Name | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-S | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone is provided.
PLAY | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 (o) | 1 | 6 (o) | Optional, where separate paediatric zone is provided. Provide baby change table.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room.
ENS-ST-C | Ensuite | Yes |  |  |  |  | 2 | 5 | 4 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
PROC | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTV | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 2 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S DTUR-10 | Dirty Utility | Yes |  |  |  |  | 1 | 8 | 1 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
TREATMENT AREAS - AMBULATORY CARE
Room Code | Room Name | SC / SC-D |  |  | 6 Ambulatory Care Spaces |  | 12 Ambulatory Care Spaces |  | 18 Ambulatory Care Spaces |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-S | Waiting - Sub | Yes |  |  |  |  | 1 | 10 | 1 | 15 | May require a public toilet if not provided nearby.
PBTR-FT | Patient Bay, Emergency - Ambulatory Care | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. One room to be attached or adjacent to a WC for Obstetrics/ Gynaecology patients.
CONS-ENT-OP | Consult - ENT / Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12-space scenario.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional. Consider locating plaster sink in Procedure Room instead if appropriate.
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 3 | 1 | 4 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 | Access to shower may also be required for areas where water immersion treatment is commonly used e.g. for jellyfish stings.
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 40-45%
OUTDOOR AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility. May be located in main ED or in the Staff Zone.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role. Consider convenient location for ambulance area.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement and qty will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit. Consider convenient location for ambulance area if dedicated ambulance Cleaner's Room is not provided.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 4 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
ED SHORT STAY UNIT
Room Code | Room Name | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation. May also be used for patients requiring palliative care.
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 4 | 5 | Provide for Class S room depending on service profile. Remainder shared between other bays/rooms.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S DTUR-10 | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 10 | Optional for 8-bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Consider adjacency to palliative care bedroom if provided in this zone.
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy.
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional.
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional.
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%