## HPU170_SoA_V4.0
HPU 170 Cardiac Investigation Unit - Schedule of Accommodation, Version 4 .0
ENTRY, RECEPTION AND WAITING AREAS
Room Code | Room Name | SC / SC-D / NS | Qty | m2 | Comments
WAIT-20 | Waiting | SC | 1 | 20 | Area recommendation is indicative and will depend on the number of services sharing the waiting area and number of people to be accommodated. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. Consider infrastructure requirements for patient self-registration and access to education/health promotion resources.
WCPU | Toilet - Public | SC | 2 | 3 | May be shared with co-located services.
WCAC | Toilet - Accessible | SC | 1 | 6 | May be shared with co-located services.
RECP-15 | Reception | SC | 1 | 15 | Size will depend on number of services being supported. Adjust area if staff are supporting both outpatient/ diagnostic and interventional areas.
BMFD-3 | Bay - Multifunction Device | SC | 1 | 3
Discounted Circulation |  |  | 25%
CARDIAC DIAGNOSTIC AREAS
Room Code | Room Name | SC / SC-D / NS | Qty | m2 | Comments
CONS | Consult Room | SC | 2 | 12 | May be flexibly used for ECG, Holter/ambulatory BP application, general consultations. Number of rooms will depend on projected activity assuming optimal utilisation.
BHWS-B | Bay - Handwashing, Type B | SC |  | 1 | Quantity is Planning Dependent Access to a handwash basin nearby will be required, e.g. corridor where not provided in Consult Rooms or other diagnostic rooms. Qty to facilitate ease of access. Assume one basin between four rooms in early planning and assess opportunities for a more efficient allocation during schematic design.
CONS | ECG / ABP / Holter Monitoring Room | SC-D | 1 | 12 | Optional as dedicated ECG / ABP / Holter Monitoring Room. Number of rooms will depend on projected activity assuming optimal utilisation. Ideally separate from Analysis Room. May be flexibly used as a Consult Room. Use CONS as a starting point.
REPR | Analysis Room - Ambulatory Monitoring | SC-D | 1 | 12 | Height adjustable desks to support 2-3 computers. Provide ECG, Holter and ABP device storage when not in use. May use Reporting Room as a starting point.
| Cardiac Implantable Electronic Device (CIED) Clinic | NS | 1 | 15 | Includes dedicated write up area and storage for programmers for different pacemakers.
STRT | Stress Testing | SC | 1 | 20 | Includes resuscitation trolley. Number of rooms will depend on projected activity. Pharmacological stress echocardiography may also be undertaken in a TOE room given a treadmill is not required.
CHPT | Change Cubicle - Patient | SC | 1 | 2
CHPT-AC | Change Cubicle - Patient, Accessible | SC | 1 | 4.5
ULTR-PR | Echocardiography - Transthoracic (TTE) | SC-D | 2 | 20 | For TTEs. Suitable for combined outpatient and inpatient cardiac diagnostic areas where cardiac ultrasound activities are undertaken. Number of rooms will depend on projected activity and case mix. Can be 16m2 if dedicated for ambulant outpatient/ diagnostic activities only (refer to ULTR as starting point).
ECHO-TOE | Echocardiography - Transoesophageal (TOE) | SC | 1 | 26 | For TOEs. May be flexibly used for TTEs also. Note recovery areas included with cath lab SOA below as an assumed integrated recovery zone.
| Reprocessing Room - High Level Disinfection, Cardiac Diagnostics | NS | 1 | 12 | Alternative Option For reprocessing of TOE probes and ultrasound transducers (TTE). Ensure dirty to clean flow. Consider opportunities for economies of scale by sharing the reprocessing area with related services e.g., CCL, Endoscopy, where appropriate.
| Reprocessing Room - High Level Disinfection, Ultrasound | NS | 1 | 7 | Alternative Option Provide in lieu of TOE/TTE Reprocessing Room for units where TOE is not performed. Ensure dirty to clean flow.
REPR | Reporting Room - Echocardiography | SC | 1 | 12 | For up to 4 people.
SSTN-10 | Staff Station | SC-D | 1 | 12 | For write-up function for non-consultant staff.
MED-14 | Medication Room | SC-D | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Media storage/prep may be located in this room based on jurisdictional policy.
CLN-10 | Clean Store | SC-D | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Media storage/prep may be located in this room based on jurisdictional policy.
DTUR-S | Dirty Utility-Sub | SC | 1 | 8 | May be shared with adjacent service.
BRES | Bay - Resuscitation Trolley | SC | 1 | 1.5
BLIN | Bay - Linen | SC | 1 | 2
BMEQ | Bay - Mobile Equipment | SC | 1 | 4
STEQ-20 | Store - Equipment | SC-D | 1 | 16 | Storage of mobile units, requires power and data. Area will depend on scope of service and no. of mobile units to be accommodated.
BWC | Trolley / Wheelchair Park | SC | 1 | 4 | May be used to store outpatient trolleys when rooms are used for inpatients. Area requirement will depend on size of unit.
Discounted Circulation |  |  | 32%
CARDIAC CATHETER LABORATORY AREAS
Room Code | Room Name | SC / SC-D / NS | Qty | m2 | Comments
CONS | Consult Room | SC | 2 | 12 | For examinations, post angiogram review, operator reviews, pre-admission interviews, consents etc. Also needs to accommodate a carer.
BHWS-B | Bay - Handwashing, Type B | SC |  | 1 | Access to a handwash basin nearby will be required, e.g. corridor where not provided in Consult Rooms or other diagnostic rooms. Qty to facilitate ease of access. Assume one basin between four rooms in early planning and assess opportunities for a more efficient allocation during schematic design).
CLAB-I | Catheter Laboratory - Interventional | SC | 2 | 55 | Assumes single plane imaging equipment. Additional 5m2 if biplane imaging equipment is required which is more commonly used for paediatrics. Adjust area to reflect project-specific higher-density procedural environment.
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SC | 1 | 60 | May have single or biplane imaging equipment. Adjust area to reflect project-specific higher-density procedural environment.
CLCR-I | Control Room - Catheter Laboratory, Interventional | SC | 2 | 14 | 1 control room per cath lab recommended.
CLCR-EP | Control Room - Catheter Laboratory, Electrophysiology Studies | SC | 1 | 17 | Required if electrophysiology studies or CIED implantations are to be performed in the cath lab. Multiple staff will stand and sit in this area. Located ideally at head or foot of bed not at the side for maximum patient and procedure visibility.
| Equipment Room - Catheter Laboratory, Interventional | NS | 2 | 10 | For storage of vendor computer cabinets. Adjust the size of the room to suit specific requirements of equipment selection.
| Equipment Room - Catheter Laboratory, Electrophysiology Studies | NS | 1 | 12 | For storage of vendor computer cabinets, additional required for EP labs. Adjust the size of the room to suit specific requirements of equipment selection.
B-SCRUB | Bay - Scrub | SC | 3 | 4 | Includes gowning requirements. May be shared between 2 labs.
| Bay - Lead Aprons | NS | 3 | 1 | One per laboratory; may be shared between rooms. To be located for ease of donning prior to accessing the procedure room.
BBW | Bay - Blanket / Fluid Warmer | SC | 1 | 1
BMEQ | Bay - Mobile Equipment | SC | 1 | 4 | Minor equipment e.g. IV poles, commodes, wheelchairs.
| Store - Sterile Stock |  | 1 | 36 | 12m2 per lab.
| Store - Contrast Media | NS | 1 | 5 | Optional Dedicated contrast media storage for CIU with high patient volume in the cath lab or echo requiring contrast. Media storage/prep may be located in other areas such as Medication Room or Clean Store based on jurisdictional policy.
STEQ-20 | Store - Equipment | SC-D | 1 | 24 | 8m2 per lab. For large equipment when not required in cath labs such as balloon pumps.
STGN | Store - General | SC-D | 1 | 8 | For storage of non-sterile bulk items/boxes.
CLNUP | Clean-up Room | SC-D | 1 | 10
REPR | Reporting Room | SC-D | 1 | 18 | 1 workstation per lab assumed, however this will depend on the staffing profile. May be shared with cardiac diagnostic services if co-located.
Room Code | Room Name | SC / SC-D | Qty | m2 | Comments
DISP-10 | Disposal Room | SC | 1 | 10 | Large volume of packaging waste. May be shared with co-located service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | SC | 1 | 5
Discounted Circulation |  |  | 32%
PATIENT HOLDING AND RECOVERY
Room Code | Room Name | SC / SC-D / NS | Qty | m2 | Comments
CHPT | Change Cubicle - Patient | SC | 2 | 2 | 1 change space per lab.
CHPT-AC | Change Cubicle - Patient, Accessible | SC | 1 | 4.5 | 1 change space per lab.
| Bay - Property, Patient | NS | 1 | 2
PT-RS1 | Patient Bay - Recovery, Stage 1 | SC |  | 9 | Quantity is Service Dependent For pre and post procedure holding and recovery. Locate to provide ease of access to lockers. The allocation and number of recovery bays should be determined based on the proposed model of care and relevant jurisdictional and project-specific requirements. As a guide: Stage 1 Recovery Bays: base on the proposed model of care, particularly the proportion of patients recovering from procedures performed under GA and whether immediate post-procedure recovery is undertaken within the CCL or in a dedicated Stage 1 Recovery area. Stage 2/3 Recovery Bays (including discharge lounge recliners): assume 3 bays per CCL and 1 - 2 bays per TOE room in early planning, depending on anticipated activity levels and patient throughput.
PT-HOLD-B | Patient Bay - Holding / Recovery Stage 2 | SC |  | 9
| Patient Bay - Discharge Lounge | NS |  | 4
WCPT | Toilet - Patient | SC | 2 | 4
WCAC | Toilet - Accessible | SC | 1 | 6
ENS-ACC | Shower / Toilet - Accessible | SC | 1 | 7 | Close access from the stress testing room and cath labs.
SSTN-14 | Staff Station | SC | 1 | 14 | Includes central monitoring.
MED-14 | Medication Room | SC-D | 1 | 8 | Shared with cath lab zone. May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | SC-D | 1 | 8 | Shared with cath lab zone. May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | SC | 4 | 1 | 1 between 4 bays.
BPATH | Bay - Pathology Point of Care Testing (POCT) | SC | 1 | 3 | Accessible from cath lab and recovery zones.
BPTS | Bay - Pneumatic Tube | SC | 1 | 1
BBW | Bay - Blanket / Fluid Warmer | SC | 1 | 1
BRES | Bay - Resuscitation | SC | 1 | 1.5
BLIN | Bay - Linen | SC | 1 | 2
BMEQ | Bay - Mobile Equipment | SC | 1 | 4
BBEV | Bay Beverage | SC | 1 | 4
DTUR-S | Dirty Utility - Sub | SC | 1 | 8
Discounted Circulation |  |  | 32%
STAFF AREAS - WORKSPACES AND AMENITIES
Room Code | Room Name | SC / SC-D / NS | Qty | m2 | Comments
OFF-1P-9 | Office - Single Person | SC |  | 9 | Quantity is Service Dependent Number will depend on staff profile and local jurisdictional policies.
OFF-WS | Office - Workstation | SC |  | 4.5 | Quantity is Service Dependent To support home monitoring service. Number of workstations will depend on staff establishment.
MEET-15 | Meeting Room | SC | 1 | 15 | Number and size will depend on requirements of unit. May be shared with adjacent service. Will require audio-visual equipment.
SRM-15 | Staff Room | SC-D | 1 | 18 | Area requirement will depend on the staff establishment. Refer to standard components for capacity requirements. Shared staff room for small units. Depending on the size of service, additional beverage bays may be needed to support staff near to where they work.
WCST | Toilet - Staff | SC | 2 | 3 | Number will suit FTE and be located in staff areas but also close to patient care rooms. Access to accessible toilet required.
CHST-10 CHST-35 | Change Room - Staff | SC-D | 1 | 30 | Indicative only; peak access periods need to be assessed; separation of overall area allocation into male and female and support for all gender/gender neutral facilities needed is in line with local policies. Includes toilets, showers, lockers; size depends on the staffing per shift.
Discounted Circulation |  |  | 25%

## IMPORT_170_SoA_V4.0_Structure
AusHFG Health Planning Unit - Schedule of Accommodation - File for Import
HPU 170 Cardiac Investigations Unit
Room Function Structure
2026-08-24
Version: V4.0
Structure Tier | Number | Name | Parent Function Full Number | Planned Areas: Gross/Net factor
Building | X | AusHFG Health Planning Units |  | 1
Department | 170 | Cardiac Investigations Unit | X | 1
Functional Group | 01 | Entry, Reception and Waiting Areas | X.170 | 1.25
Functional Group | 02 | Cardiac Diagnostic Areas | X.170 | 1.32
Functional Group | 03 | Cardiac Catheter Laboratory Areas | X.170 | 1.32
Functional Group | 04 | Patient Holding and Recovery | X.170 | 1.32
Functional Group | 05 | Staff Areas - Workspaces and Amenities | X.170 | 1.25

## IMPORT_170_SoA_V4.0_Rooms
AusHFG Health Planning Unit - Schedule of Accommodation - File for Import
HPU 170 Cardiac Investigations Unit
Room List
2026-08-24
Version: V4.0
Building (Number) | Building (Name) | HPU (Number) | HPU (Name) | Functional Group (Number) | Functional Group (Name) | Serial Number | Room Name | Room Code | Area AusHFG | Programmed Area | Ceiling Height | AusHFG SC / SC-D | Optional | Room Comment | Room Data Status | FFE: Status | SER: Status | FIN: Status | D+W: Status | MSP: Status
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 01 | Entry, Reception and Waiting Areas | 001 | Waiting | WAIT-20 | 20 | 20 | 2.7 | SC |  | Area recommendation is indicative and will depend on the number of services sharing the waiting area and number of people to be accommodated. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. Consider infrastructure requirements for patient self-registration and access to education/health promotion resources. | WAIT-20 | WAIT-20 | WAIT-20 | WAIT-20 | WAIT-20 | WAIT-20
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 01 | Entry, Reception and Waiting Areas | 002 | Toilet - Public | WCPU | 3 | 3 | 2.7 | SC |  | May be shared with co-located services. | WCPU | WCPU | WCPU | WCPU | WCPU | WCPU
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 01 | Entry, Reception and Waiting Areas | 003 | Toilet - Public | WCPU | 3 | 3 | 2.7 | SC |  | May be shared with co-located services. | WCPU | WCPU | WCPU | WCPU | WCPU | WCPU
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 01 | Entry, Reception and Waiting Areas | 004 | Toilet - Accessible | WCAC | 6 | 6 | 2.7 | SC |  | May be shared with co-located services. | WCAC | WCAC | WCAC | WCAC | WCAC | WCAC
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 01 | Entry, Reception and Waiting Areas | 005 | Reception | RECP-15 | 15 | 15 | 2.7 | SC |  | Size will depend on number of services being supported. Adjust area if staff are supporting both outpatient/diagnostic and interventional areas. | RECP-15 | RECP-15 | RECP-15 | RECP-15 | RECP-15 | RECP-15
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 01 | Entry, Reception and Waiting Areas | 006 | Bay - Multifunction Device | BMFD-3 | 3 | 3 | 2.7 | SC |  |  | BMFD-3 | BMFD-3 | BMFD-3 | BMFD-3 | BMFD-3 | BMFD-3
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 007 | Consult Room | CONS | 12 | 12 | 2.7 | SC |  | May be flexibly used for ECG, Holter/ambulatory BP application, general consultations. Number of rooms will depend on projected activity assuming optimal utilisation. | CONS | CONS | CONS | CONS | CONS | CONS
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 008 | Consult Room | CONS | 12 | 12 | 2.7 | SC |  | May be flexibly used for ECG, Holter/ambulatory BP application, general consultations. Number of rooms will depend on projected activity assuming optimal utilisation. | CONS | CONS | CONS | CONS | CONS | CONS
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 009 | Bay - Handwashing, Type B | BHWS-B | 1 | 1 | 2.7 | SC | Quantity is Planning Dependent | Quantity is Planning Dependent Access to a handwash basin nearby will be required, e.g. corridor where not provided in Consult Rooms or other diagnostic rooms. Qty to facilitate ease of access. Assume one basin between four rooms in early planning and assess opportunities for a more efficient allocation during schematic design). | BHWS-B | BHWS-B | BHWS-B | BHWS-B | BHWS-B | BHWS-B
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 010 | ECG / ABP / Holter Monitoring Room | CONS | 12 | 12 | 2.7 | SC-D | Optional | Optional as dedicated ECG / ABP / Holter Monitoring Room. Number of rooms will depend on projected activity assuming optimal utilisation. Ideally separate from Analysis Room. May be flexibly used as a Consult Room. Use CONS as a starting point. | CONS | CONS | CONS | CONS | CONS | CONS
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 011 | Analysis Room - Ambulatory Monitoring | REPR | 12 | 12 | 2.7 | SC-D |  | Height adjustable desks to support 2-3 computers. Provide ECG, Holter and ABP device storage when not in use. May use Reporting Room as a starting point. | REPR | REPR | REPR | REPR | REPR | REPR
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 012 | Cardiac Implantable Electronic Device (CIED) Clinic |  | 15 | 15 |  | NS |  | Includes dedicated write up area and storage for programmers for different pacemakers.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 013 | Stress Testing | STRT | 20 | 20 | 2.7 | SC |  | Includes resuscitation trolley. Number of rooms will depend on projected activity. Pharmacological stress echocardiography may also be undertaken in a TOE room given a treadmill is not required. | STRT | STRT | STRT | STRT | STRT | STRT
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 014 | Change Cubicle - Patient | CHPT | 2 | 2 | 2.7 | SC |  |  | CHPT | CHPT | CHPT | CHPT | CHPT | CHPT
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 015 | Change Cubicle - Patient, Accessible | CHPT-AC | 4.5 | 4.5 | 2.7 | SC |  |  | CHPT-AC | CHPT-AC | CHPT-AC | CHPT-AC | CHPT-AC | CHPT-AC
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 016 | Echocardiography - Transthoracic (TTE) | ULTR-PR | 20 | 20 | 2.7 | SC-D |  | For TTEs. Suitable for combined outpatient and inpatient cardiac diagnostic areas where cardiac ultrasound activities are undertaken. Number of rooms will depend on projected activity and case mix.Can be 16m2 if dedicated for ambulant outpatient/ diagnostic activities only (refer to ULTR as starting point). | ULTR-PR | ULTR-PR | ULTR-PR | ULTR-PR | ULTR-PR | ULTR-PR
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 017 | Echocardiography - Transthoracic (TTE) | ULTR-PR | 20 | 20 | 2.7 | SC-D |  | For TTEs. Suitable for combined outpatient and inpatient cardiac diagnostic areas where cardiac ultrasound activities are undertaken. Number of rooms will depend on projected activity and case mix.Can be 16m2 if dedicated for ambulant outpatient/ diagnostic activities only (refer to ULTR as starting point). | ULTR-PR | ULTR-PR | ULTR-PR | ULTR-PR | ULTR-PR | ULTR-PR
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 018 | Echocardiography - Transoesophageal (TOE) | ECHO-TOE | 26 | 26 | 2.7 | SC |  | For TOEs. May be flexibly used for TTEs also. Note recovery areas included with cath lab SOA below as an assumed integrated recovery zone. | ECHO-TOE | ECHO-TOE | ECHO-TOE | ECHO-TOE | ECHO-TOE | ECHO-TOE
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 019 | Reprocessing Room - High Level Disinfection, Cardiac Diagnostics |  | 12 | 12 |  | NS | Alternative Option | Alternative Option For reprocessing of TOE probes and ultrasound transducers (TTE). Ensure dirty to clean flow. Consider opportunities for economies of scale by sharing the reprocessing area with related services e.g., CCL, Endoscopy, where appropriate.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 020 | Reprocessing Room - High Level Disinfection, Ultrasound |  | 7 | 7 |  | NS | Alternative Option | Alternative Option Provide in lieu of TOE/TTE Reprocessing Room for units where TOE is not performed.Ensure dirty to clean flow.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 021 | Reporting Room - Echocardiography | REPR | 12 | 12 | 2.7 | SC |  | For up to 4 people. | REPR | REPR | REPR | REPR | REPR | REPR
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 022 | Staff Station | SSTN-10 | 10 | 10 | 2.7 | SC-D |  | For write-up function for non-consultant staff. | SSTN-10 | SSTN-10 | SSTN-10 | SSTN-10 | SSTN-10 | SSTN-10
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 023 | Medication Room | MED-14 | 8 | 8 | 2.7 | SC-D |  | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.Media storage/prep may be located in this room based on jurisdictional policy. | MED-14 | MED-14 | MED-14 | MED-14 | MED-14 | MED-14
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 024 | Clean Store | CLN-10 | 8 | 8 | 2.7 | SC-D |  | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.Media storage/prep may be located in this room based on jurisdictional policy. | CLN-10 | CLN-10 | CLN-10 | CLN-10 | CLN-10 | CLN-10
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 025 | Dirty Utility, Sub | DTUR-S | 8 | 8 | 2.7 | SC |  | May be shared with adjacent service. | DTUR-S | DTUR-S | DTUR-S | DTUR-S | DTUR-S | DTUR-S
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 026 | Bay - Resuscitation Trolley | BRES | 1.5 | 1.5 | 2.7 | SC |  |  | BRES | BRES | BRES | BRES | BRES | BRES
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 027 | Bay - Linen | BLIN | 2 | 2 | 2.7 | SC |  |  | BLIN | BLIN | BLIN | BLIN | BLIN | BLIN
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 028 | Bay - Mobile Equipment | BMEQ | 4 | 4 | 2.7 | SC |  |  | BMEQ | BMEQ | BMEQ | BMEQ | BMEQ | BMEQ
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 029 | Store - Equipment | STEQ-20 | 16 | 16 | 2.7 | SC-D |  | Storage of mobile units, requires power and data. Area will depend on scope of service and no. of mobile units to be accommodated. | STEQ-20 | STEQ-20 | STEQ-20 | STEQ-20 | STEQ-20 | STEQ-20
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 02 | Cardiac Diagnostic Areas | 030 | Trolley / Wheelchair Park | BWC | 4 | 4 | 2.7 | SC |  | May be used to store outpatient trolleys when rooms are used for inpatients. Area requirement will depend on size of unit. | BWC | BWC | BWC | BWC | BWC | BWC
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 031 | Consult Room | CONS | 12 | 12 | 2.7 | SC |  | For examinations, post angiogram review, operator reviews, pre-admission interviews, consents etc. Also needs to accommodate a carer. | CONS | CONS | CONS | CONS | CONS | CONS
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 032 | Consult Room | CONS | 12 | 12 | 2.7 | SC |  | For examinations, post angiogram review, operator reviews, pre-admission interviews, consents etc. Also needs to accommodate a carer. | CONS | CONS | CONS | CONS | CONS | CONS
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 033 | Bay - Handwashing, Type B | BHWS-B | 1 | 1 | 2.7 | SC |  | Access to a handwash basin nearby will be required, e.g. corridor where not provided in Consult Rooms or other diagnostic rooms. Qty to facilitate ease of access. Assume one basin between four rooms in early planning and assess opportunities for a more efficient allocation during schematic design). | BHWS-B | BHWS-B | BHWS-B | BHWS-B | BHWS-B | BHWS-B
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 034 | Catheter Laboratory - Interventional | CLAB-I | 55 | 55 | 3 | SC |  | Assumes single plane imaging equipment. Additional 5m2 if biplane imaging equipment is required which is more commonly used for paediatrics.Adjust area to reflect project-specific higher-density procedural environment. | CLAB-I | CLAB-I | CLAB-I | CLAB-I | CLAB-I | CLAB-I
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 035 | Catheter Laboratory - Interventional | CLAB-I | 55 | 55 | 3 | SC |  | Assumes single plane imaging equipment. Additional 5m2 if biplane imaging equipment is required which is more commonly used for paediatrics.Adjust area to reflect project-specific higher-density procedural environment. | CLAB-I | CLAB-I | CLAB-I | CLAB-I | CLAB-I | CLAB-I
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 036 | Catheter Laboratory - Electrophysiology Studies | CLAB-EP | 60 | 60 | 3 | SC |  | May have single or biplane imaging equipment. Adjust area to reflect project-specific higher-density procedural environment. | CLAB-EP | CLAB-EP | CLAB-EP | CLAB-EP | CLAB-EP | CLAB-EP
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 037 | Control Room - Catheter Laboratory, Interventional | CLCR-I | 14 | 14 | 2.7 | SC |  | 1 control room per cath lab recommended. | CLCR-I | CLCR-I | CLCR-I | CLCR-I | CLCR-I | CLCR-I
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 038 | Control Room - Catheter Laboratory, Interventional | CLCR-I | 14 | 14 | 2.7 | SC |  | 1 control room per cath lab recommended. | CLCR-I | CLCR-I | CLCR-I | CLCR-I | CLCR-I | CLCR-I
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 039 | Control Room - Catheter Laboratory, Electrophysiology Studies | CLCR-EP | 17 | 17 | 2.7 | SC |  | Required if electrophysiology studies or CIED implantations are to be performed in the cath lab. Multiple staff will stand and sit in this area. Located ideally at head or foot of bed not at the side for maximum patient and procedure visibility. | CLCR-EP | CLCR-EP | CLCR-EP | CLCR-EP | CLCR-EP | CLCR-EP
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 040 | Equipment Room - Catheter Laboratory, Interventional |  | 10 | 10 |  | NS |  | For storage of vendor computer cabinets. Adjust the size of the room to suit specific requirements of equipment selection.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 041 | Equipment Room - Catheter Laboratory, Interventional |  | 10 | 10 |  | NS |  | For storage of vendor computer cabinets. Adjust the size of the room to suit specific requirements of equipment selection.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 042 | Equipment Room - Catheter Laboratory, Electrophysiology Studies |  | 12 | 12 |  | NS |  | For storage of vendor computer cabinets, additional required for EP labs. Adjust the size of the room to suit specific requirements of equipment selection.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 043 | Bay - Scrub | B-SCRUB | 4 | 4 | 2.7 | SC |  | Includes gowning requirements. May be shared between 2 labs. | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 044 | Bay - Scrub | B-SCRUB | 4 | 4 | 2.7 | SC |  | Includes gowning requirements. May be shared between 2 labs. | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 045 | Bay - Scrub | B-SCRUB | 4 | 4 | 2.7 | SC |  | Includes gowning requirements. May be shared between 2 labs. | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB | B-SCRUB
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 046 | Bay - Lead Aprons |  | 1 | 1 |  | NS |  | One per laboratory; may be shared between rooms. To be located for ease of donning prior to accessing the procedure room.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 047 | Bay - Lead Aprons |  | 1 | 1 |  | NS |  | One per laboratory; may be shared between rooms. To be located for ease of donning prior to accessing the procedure room.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 048 | Bay - Lead Aprons |  | 1 | 1 |  | NS |  | One per laboratory; may be shared between rooms. To be located for ease of donning prior to accessing the procedure room.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 049 | Bay - Blanket / Fluid Warmer | BBW | 1 | 1 | 2.7 | SC |  |  | BBW | BBW | BBW | BBW | BBW | BBW
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 050 | Bay - Mobile Equipment | BMEQ | 4 | 4 | 2.7 | SC |  | Minor equipment e.g. IV poles, commodes, wheelchairs. | BMEQ | BMEQ | BMEQ | BMEQ | BMEQ | BMEQ
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 051 | Store - Sterile Stock | STSS | 36 | 36 |  | SC-D |  | 12m2 per lab. | STSS | STSS | STSS | STSS | STSS | STSS
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 052 | Store - Contrast Media |  | 5 | 5 |  | NS | Optional | Optional Dedicated contrast media storage for CIU with high patient volume in the cath lab or echo requiring contrast. Media storage/prep may be located in other areas such as Medication Room or Clean Store based on jurisdictional policy.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 053 | Store - Equipment | STEQ-20 | 24 | 24 | 2.7 | SC-D |  | 8m2 per lab. For large equipment when not required in cath labs such as balloon pumps. | STEQ-20 | STEQ-20 | STEQ-20 | STEQ-20 | STEQ-20 | STEQ-20
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 054 | Store - General | STGN | 9 | 9 | 2.7 | SC-D |  | For storage of non-sterile bulk items/boxes. | STGN | STGN | STGN | STGN | STGN | STGN
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 055 | Clean-Up Room | CLNUP | 10 | 10 | 2.7 | SC-D |  |  | CLNUP | CLNUP | CLNUP | CLNUP | CLNUP | CLNUP
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 056 | Reporting Room | REPR | 18 | 18 | 2.7 | SC-D |  | 1 workstation per lab assumed, however this will depend on the staffing profile. May be shared with cardiac diagnostic services if co-located. | REPR | REPR | REPR | REPR | REPR | REPR
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 057 | Disposal Room | DISP-10 | 10 | 10 | 2.7 | SC |  | Large volume of packaging waste. May be shared with co-located service.Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes. | DISP-10 | DISP-10 | DISP-10 | DISP-10 | DISP-10 | DISP-10
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 03 | Cardiac Catheter Laboratory Areas | 058 | Cleaner's Room | CLRM | 5 | 5 | 2.7 | SC |  |  | CLRM | CLRM | CLRM | CLRM | CLRM | CLRM
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 059 | Change Cubicle - Patient | CHPT | 2 | 2 | 2.7 | SC |  | 1 change space per lab. | CHPT | CHPT | CHPT | CHPT | CHPT | CHPT
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 060 | Change Cubicle - Patient | CHPT | 2 | 2 | 2.7 | SC |  | 1 change space per lab. | CHPT | CHPT | CHPT | CHPT | CHPT | CHPT
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 061 | Change Cubicle - Patient, Accessible | CHPT-AC | 4.5 | 4.5 | 2.7 | SC |  | 1 change space per lab. | CHPT-AC | CHPT-AC | CHPT-AC | CHPT-AC | CHPT-AC | CHPT-AC
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 062 | Bay - Property, Patient |  | 2 | 2 |  | NS
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 063 | Patient Bay - Recovery, Stage 1 | PT-RS1 | 9 | 9 | 2.7 | SC | Quantity is Service Dependent | Quantity is Service Dependent For pre and post procedure holding and recovery. Locate to provide ease of access to lockers. The allocation and number of recovery bays should be determined based on the proposed model of care and relevant jurisdictional and project-specific requirements. As a guide: Stage 1 Recovery Bays: based on the proposed model of care, particularly the proportion of patients recovering from procedures performed under GA and whether immediate post-procedure recovery is undertaken within the CCL or in a dedicated Stage 1 Recovery area. Stage 2/3 Recovery Bays (including discharge lounge recliners): assume 3 bays per CCL and 1 - 2 bays per TOE room in early planning, depending on anticipated activity levels and patient throughput. | PT-RS1 | PT-RS1 | PT-RS1 | PT-RS1 | PT-RS1 | PT-RS1
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 064 | Patient Bay - Holding, Bed | PT-HOLD-B | 9 | 9 | 2.7 | SC | Quantity is Service Dependent | Quantity is Service Dependent For pre and post procedure holding and recovery. Locate to provide ease of access to lockers. The allocation and number of recovery bays should be determined based on the proposed model of care and relevant jurisdictional and project-specific requirements. As a guide: Stage 1 Recovery Bays: based on the proposed model of care, particularly the proportion of patients recovering from procedures performed under GA and whether immediate post-procedure recovery is undertaken within the CCL or in a dedicated Stage 1 Recovery area. Stage 2/3 Recovery Bays (including discharge lounge recliners): assume 3 bays per CCL and 1 - 2 bays per TOE room in early planning, depending on anticipated activity levels and patient throughput. | PT-HOLD-B | PT-HOLD-B | PT-HOLD-B | PT-HOLD-B | PT-HOLD-B | PT-HOLD-B
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 065 | Patient Bay - Discharge Lounge |  | 4 | 4 | 2.7 | NS | Quantity is Service Dependent | Quantity is Service Dependent For pre and post procedure holding and recovery. Locate to provide ease of access to lockers. The allocation and number of recovery bays should be determined based on the proposed model of care and relevant jurisdictional and project-specific requirements. As a guide: Stage 1 Recovery Bays: based on the proposed model of care, particularly the proportion of patients recovering from procedures performed under GA and whether immediate post-procedure recovery is undertaken within the CCL or in a dedicated Stage 1 Recovery area. Stage 2/3 Recovery Bays (including discharge lounge recliners): assume 3 bays per CCL and 1 - 2 bays per TOE room in early planning, depending on anticipated activity levels and patient throughput.
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 066 | Toilet - Patient | WCPT | 4 | 4 | 2.7 | SC |  |  | WCPT | WCPT | WCPT | WCPT | WCPT | WCPT
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 067 | Toilet - Patient | WCPT | 4 | 4 | 2.7 | SC |  |  | WCPT | WCPT | WCPT | WCPT | WCPT | WCPT
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 068 | Toilet - Accessible | WCAC | 6 | 6 | 2.7 | SC |  |  | WCAC | WCAC | WCAC | WCAC | WCAC | WCAC
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 069 | Shower / Toilet - Accessible | ENS-ACC | 7 | 7 | 2.7 | SC |  | Close access from the stress testing room and cath labs. | ENS-ACC | ENS-ACC | ENS-ACC | ENS-ACC | ENS-ACC | ENS-ACC
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 04 | Patient Holding and Recovery | 070 | Staff Station | SSTN-14 | 14 | 14 | 2.7 | SC |  | Includes central monitoring. | SSTN-14 | SSTN-14 | SSTN-14 | SSTN-14 | SSTN-14 | SSTN-14
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 05 | Staff Areas - Workspaces and Amenities | 071 | Office - 1 Person | OFF-1P-9 | 9 | 9 | 2.7 | SC | Quantity is Service Dependent | Quantity is Service Dependent Number will depend on staff profile and local jurisdictional policies. | OFF-1P-9 | OFF-1P-9 | OFF-1P-9 | OFF-1P-9 | OFF-1P-9 | OFF-1P-9
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 05 | Staff Areas - Workspaces and Amenities | 072 | Office - Workstation | OFF-WS | 4.5 | 4.5 | 2.7 | SC | Quantity is Service Dependent | Quantity is Service Dependent To support home monitoring service. Number of workstations will depend on staff establishment. | OFF-WS | OFF-WS | OFF-WS | OFF-WS | OFF-WS | OFF-WS
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 05 | Staff Areas - Workspaces and Amenities | 073 | Meeting Room | MEET-15 | 15 | 15 | 2.7 | SC |  | Number and size will depend on requirements of unit. May be shared with adjacent service. Will require audio-visual equipment. | MEET-15 | MEET-15 | MEET-15 | MEET-15 | MEET-15 | MEET-15
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 05 | Staff Areas - Workspaces and Amenities | 074 | Staff Room | SRM-15 | 18 | 18 | 2.7 | SC-D |  | Area requirement will depend on the staff establishment. Refer to standard components for capacity requirements. Shared staff room for small units. Depending on the size of service, additional beverage bays may be needed to support staff near to where they work. | SRM-15 | SRM-15 | SRM-15 | SRM-15 | SRM-15 | SRM-15
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 05 | Staff Areas - Workspaces and Amenities | 075 | Toilet - Staff | WCST | 3 | 3 | 2.7 | SC |  | Number will suit FTE and be located in staff areas but also close to patient care rooms. Access to accessible toilet required. | WCST | WCST | WCST | WCST | WCST | WCST
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 05 | Staff Areas - Workspaces and Amenities | 076 | Toilet - Staff | WCST | 3 | 3 | 2.7 | SC |  | Number will suit FTE and be located in staff areas but also close to patient care rooms. Access to accessible toilet required. | WCST | WCST | WCST | WCST | WCST | WCST
X | AusHFG Health Planning Units | 170 | Cardiac Investigations Unit | 05 | Staff Areas - Workspaces and Amenities | 077 | Change - Staff | CHST-10, CHST-35 | 30 | 30 | 2.7 | SC-D |  | Indicative only; peak access periods need to be assessed; separation of overall area allocation into male and female and support for all gender/gender neutral facilities needed is in line with local policies. Includes toilets, showers, lockers; size depends on the staffing per shift. | CHST-35 | CHST-35 | CHST-35 | CHST-35 | CHST-35 | CHST-35