## 2 Steam Sterilizers
STERILIZING SERVICES UNIT - 2 STEAM STERILIZERS
Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
ENTRY
OFF-S9 | Office - Single Person, 9m2 | Yes | 1 | 9 | Unit manager
OFF-S12 | Office - 2 Person, Shared, 12m2 | Yes | 0
STPS-8 | Store - Photocopy / Stationery, 8m2 | Yes | 1 | 8 | Adjacent to the reception/clerical area. Accessible to other staff as well
| Discounted Circulation |  |  | 20%
PROCESSING AREAS
Receiving/ Cleaning/ Decontamination
| Loan Equipment - Receipt/ Dispatch |  | 1 | 35 | Include only where loan equipment is used. Refer Note 1
| Receiving Area - Used Items |  | 1 | 20 | Refer Note 1
| Trolley Wash |  | 1 | 15 | An additional trolley wash unit may be required to support larger services
| Cleaning / Decontamination |  | 1 | 60 | Refer Note 2
| Discounted Circulation |  |  | 20%
Packing/ Sterilization
| Packing / Clean Workroom |  | 1 | 60
| Sterilizer - Steam |  | 1 | 20 | Includes plant
| Sterilizer Loading / Unloading/ Cooling |  | 1 | 30 | Plus spare trolleys
| Sterilizer - ETO |  | 0 |  | Free standing plus anteroom, aeration cabinet and plant. Many services will not use this equipment and replace with alternatives such as other low temperature technology
| Sterilizer - Low Temperature |  | 1 | 6 | Free-standing. No. larger services needs to be determined as multiple units may be used.
Dispatch
| Dispatch - other clinical services |  | 1 | 10 | e.g. IPUs, ED and Critical Care Units. Assumes RMD are returned and stored at the point of use.
| Dispatch – Operating Theatres |  | 1 | 20 | Should be contiguous with Sterilizer Loading / Unloading/ Cooling. Assumes RMD are returned and stored in Operating Theatres
| Discounted Circulation |  |  | 20%
SUPPORT AREAS
DISP-8 | Disposal room | Yes | 1 | 8 | Access to external corridor
STGN-9 | Store – General | Yes | 1 | 12 | Bulk goods receipt, deboxing, linen
CLRM-5 | Cleaners Room, 5m2 | Yes | 1 | 5 | Within Unit
| Discounted Circulation |  |  | 20%
STAFF AREAS
WCST | Toilet – Staff, 3m2 | Yes |  | 3 | No. to suit staff numbers.
CHST-10 | Change – Staff, 10m2 | Yes | 2 | 10 | Could be shared with adjacent OR. Includes shower, toilet and lockers
SMR-15 | Staff Room | Yes | 1 | 12 | Could be shared with adjacent OR
MEET-15 | Meeting Room | Yes | 0
| Discounted Circulation |  |  | 20%

## 4 Steam Sterilizers
STERILIZING SERVICES UNIT - 4 STEAM STERILIZERS
Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
ENTRY
OFF-S9 | Office - Single Person, 9m2 | Yes | 1 | 9 | Unit manager
OFF-S12 | Office - 2 Person, Shared, 12m2 | Yes | 1 | 12 (o)
STPS-8 | Store - Photocopy / Stationery, 8m2 | Yes | 1 | 8 | Adjacent to the reception/clerical area. Accessible to other staff as well
| Discounted Circulation |  |  | 20%
PROCESSING AREAS
Receiving/ Cleaning/ Decontamination
| Loan Equipment - Receipt/ Dispatch |  | 1 | 50 | Include only where loan equipment is used. Refer Note 1
| Receiving Area - Used Items |  | 1 | 35 | Refer Note 1
| Trolley Wash |  | 1 | 15 | An additional trolley wash unit may be required to support larger services
| Cleaning / Decontamination |  | 1 | 95 | Refer Note 2
| Discounted Circulation |  |  | 20%
Packing/ Sterilization
| Packing / Clean Workroom |  | 1 | 95
| Sterilizer - Steam |  | 1 | 40 | Includes plant
| Sterilizer Loading / Unloading/ Cooling |  | 1 | 60 | Plus spare trolleys
| Sterilizer - ETO |  | 1 | 25 (o) | Free standing plus anteroom, aeration cabinet and plant. Many services will not use this equipment and replace with alternatives such as other low temperature technology
| Sterilizer - Low Temperature |  |  | 6 | Free-standing. No. larger services needs to be determined as multiple units may be used.
Dispatch
| Dispatch - other clinical services |  | 1 | 15 | e.g. IPUs, ED and Critical Care Units. Assumes RMD are returned and stored at the point of use.
| Dispatch – Operating Theatres |  | 1 | 40 | Should be contiguous with Sterilizer Loading / Unloading/ Cooling. Assumes RMD are returned and stored in Operating Theatres
| Discounted Circulation |  |  | 20%
SUPPORT AREAS
DISP-8 | Disposal room | Yes | 1 | 10 | Access to external corridor
STGN-9 | Store – General | Yes | 1 | 20 | Bulk goods receipt, deboxing, linen
CLRM-5 | Cleaners Room, 5m2 | Yes | 1 | 5 | Within Unit
| Discounted Circulation |  |  | 20%
STAFF AREAS
WCST | Toilet – Staff, 3m2 | Yes |  | 3 | No. to suit staff numbers.
CHST-10 | Change – Staff, 10m2 | Yes | 2 | 14 | Could be shared with adjacent OR. Includes shower, toilet and lockers
SMR-15 | Staff Room | Yes | 1 | 15 | Could be shared with adjacent OR
MEET-15 | Meeting Room | Yes | 1 | 15
| Discounted Circulation |  |  | 20%

## Endoscopy Reprocessing 2
ENDOSCOPE REPROCESSING UNIT - 2 ROOMS
Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
| Scope Reprocessing – dirty zone | Yes | 1 | 8
| Scope Reprocessing – clean zone | Yes | 1 | 9 | If possible, direct access from Endoscopy Rooms
| Endoscope Store | Yes | 1 | 2 | This may be located with the clean zone with pass through cupboards used so that clinical staff can easily retrieve scopes without entering.
| Discounted Circulation |  |  | 20%

## Endoscopy Reprocess 4
ENDOSCOPE REPROCESSING UNIT - 4 ROOMS
Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
| Scope Reprocessing – dirty zone | Yes | 1 | 10
| Scope Reprocessing – clean zone | Yes | 1 | 12 | If possible, direct access from Endoscopy Rooms
| Endoscope Store | Yes | 1 | 4 | This may be located with the clean zone with pass through cupboards used so that clinical staff can easily retrieve scopes without entering.
| Discounted Circulation |  |  | 20%