## Level 1
Intensive Care General - Level 1
AusHFG Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
ENTRY / RECEPTION
INTF | Interview Room | Yes | 1 | 12 | For interviews with relatives
MEET-12 | Meeting Room | Yes |  | - | For interviews with relatives.
WCPU-3 | Toilet - Public, 3m2 | Yes | 1 | 3
WAIT-10 | Waiting, 10m2 | Yes | 1 | 10 | Nominal area. To be calculated at 1.2m2 per able- bodied person, 1.5m2 per wheelchair occupant.
| Discounted Circulation % |  | 25%
PATIENT AREAS
PBC-24 | Patient Bay - Critical, 24m2 | Yes |  | 24 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
PBC-20 | Patient Bay - Critical, 20m2 | Yes |  | 20 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
PBCE-25 | Patient Bay - Critical (Enclosed), 20m2 | Yes |  | 25 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
| Patient Bay - Critical Enclosed (Class N Isolation) |  |  | 25 | No. dependent on services planning ; clustered, located away from Unit entrance.
ANRM | Anteroom | Yes |  | 6 | Attached to 1 Bed Rooms - Isolation Class N (neg pressure ventilation)
BATH | Bathroom | Yes | 1 | 15 | Inclusion depends on operational policy of unit
BLIN | Bay - Linen | Yes | 1 | 2
BRES | Bay - Resuscitation | Yes | 1 | 1.5
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 4
ENS-SP | Ensuite - Special, 6m2 | Yes | 1 | 6 | FPU; sizes for ‘full assistance’ i.e. 2 staff plus medical equipment.
| Discounted Circulation % |  | 40%
STAFF AREAS
MEET-L-20 | Meeting Room, 20m2 | Yes | Shared |  | Education / resource / teleheath - may include library, 24 hour access required via perimeter of unit.
MEET-L-30 | Meeting Room, 30m2 | Yes | 1 | 15 | Seminar / Training Room - alternative location for Library 24 hour access required; perimeter of unit.
OFF-CLW | Office – Clinical Workroom | Yes |  |  | Inclusion depends on operational policy of unit. Close to staff station
OFF-S9 | Office - Single Person, 9m2 | Yes |  |  | Senior Nurse Manager, NUM, staff specialists
OFF-S12 | Office - Single Person, 12m2 | Yes |  |  | Medical Director
| Office - Workstation, 4.4m2 |  |  | 4.4 | Registrars - workstation/s, open plan or enclosed. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | CNC/Educator-workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  |  | Research - workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | Secretarial - workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | General - workstation/s open plan or in shared office. Number determined by staffing.
OVBR | Overnight Stay - Bedroom | Yes |  |  | Registrar, needs access to bathroom facilities e.g. Staff Change Rooms
SHST | Shower - Staff, 3m2 | Yes | Shared
SRM-15 | Staff Room, 15m2 | Yes | 1 | 15
SSTN | Staff Station, 20m2 | Yes | 1 | 18
CHST-10 | Change - Staff (Male / Female), 10m2 | Yes | 1 | 8 | Includes toilets, showers, lockers; size depends on the staffing per shift. (Female)
CHST-10 | Change - Staff (Male / Female), 10m2 | Yes | 1 | 8 | Includes toilets, showers, lockers; size depends on staffing per shift. (Male)
STFS-10 | Store- Files, 10m2 | Yes
STPS-8 | Store - Photocopy / Stationery, 8m2 | Yes | 1 | 5
| Discounted Circulation % |  | 25%
SUPPORT AREAS
BBW | Bay - Blanket / Fluid Warming | Yes |  |  | Inclusion depends on operational policy of unit.
BHWS-A | Bay - Handwashing, Type A | Yes |  | 1 | Refer to Part D for numbers and locations
BMEQ-4 | Bay - Mobile Equipment, 4m2 | Yes | 2 | 4 | Locate in quiet low traffic areas.
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes
BPATH | Bay - Pathology |  |  |  | Inclusion depends on operational policy of unit
BPTS | Bay - Pneumatic Tube |  | 1 | 1
CLRM-5 | Cleaner's Room, 5m2 | Yes | 1 | 5
CLUR-12 | Clean Utility, 12m2 | Yes | 1 | 12
DTUR-10 | Dirty Utility, 10m2 | Yes | 1 | 10
DISP-8 | Disposal Room, 8m2 | Yes | 1 | 8 | Inclusion depends on bed numbers and waste management guidelines. Preference for only 1 larger room.
CLUP-7 | Clean-Up Room, 7m2 | Yes | 1 | 7
| Respiratory / Biomedical Workroom |  |  |  | Inclusion depends on operational guidelines of unit.
STDR-10 | Medication Room, 10m2 | Yes | 1 | 10 | May be included with clean utility
STEQ-14 | Store - Equipment, 14m2 | Yes | 1 | 14 | General equipment
STEQ-20 | Store - Equipment, 20m2 | Yes |  |  | Inclusion depends on operational guidelines of unit. Required for storage of respiratory associated equipment and consumables.
STSS-30 | Store - Sterile Stock, 30m2 | Yes | 1 | 15
| Workroom - Telehealth |  |  |  | Optional: Inclusion depends on operational guideline of unit. Can be used for viewing medical images and discussions, and for telehealth activities for liaison regarding transfers, virtual rounds etc.
| Discounted Circulation % |  | 25%

## Level 2
Intensive Care General - Level 2
AusHFG Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
ENTRY / RECEPTION
INTF | Interview Room | Yes |  | - | For interviews with relatives
MEET-12 | Meeting Room | Yes | 1 | 15 | For interviews with relatives.
WCPU-3 | Toilet - Public, 3m2 | Yes | 1 | 3
WAIT-10 | Waiting, 10m2 | Yes | 1 | 15 | Nominal area. To be calculated at 1.2m2 per able- bodied person, 1.5m2 per wheelchair occupant.
| Discounted Circulation % |  | 25%
PATIENT AREAS
PBC-24 | Patient Bay - Critical, 24m2 | Yes |  | 24 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
PBC-20 | Patient Bay - Critical, 20m2 | Yes |  | 20 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
PBCE-25 | Patient Bay - Critical (Enclosed), 20m2 | Yes |  | 25 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
| Patient Bay - Critical Enclosed (Class N Isolation) |  |  | 25 | No. dependent on services planning ; clustered, located away from Unit entrance.
ANRM | Anteroom | Yes |  | 6 | Attached to 1 Bed Rooms - Isolation Class N (neg pressure ventilation)
BATH | Bathroom | Yes | 1 | 15 | Inclusion depends on operational policy of unit
BLIN | Bay - Linen | Yes | 2 | 2
BRES | Bay - Resuscitation | Yes | 2 | 1.5
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 5
ENS-SP | Ensuite - Special, 6m2 | Yes | 1 | 6 | FPU; sizes for ‘full assistance’ i.e. 2 staff plus medical equipment.
| Discounted Circulation % |  | 40%
STAFF AREAS
MEET-L-20 | Meeting Room, 20m2 | Yes | 1 | 20 | Education / resource / teleheath - may include library, 24 hour access required via perimeter of unit.
MEET-L-30 | Meeting Room, 30m2 | Yes | 1 | 30 | Seminar / Training Room - alternative location for Library 24 hour access required; perimeter of unit.
OFF-CLW | Office – Clinical Workroom | Yes | 1 | 15 | Inclusion depends on operational policy of unit. Close to staff station
OFF-S9 | Office - Single Person, 9m2 | Yes |  | 9 | Senior Nurse Manager, NUM, staff specialists
OFF-S12 | Office - Single Person, 12m2 | Yes | 1 | 12 | Medical Director
| Office - Workstation, 4.4m2 |  |  | 4.4 | Registrars - workstation/s, open plan or enclosed. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | CNC/Educator-workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | Research - workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | Secretarial - workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | General - workstation/s open plan or in shared office. Number determined by staffing.
OVBR | Overnight Stay - Bedroom | Yes | 1 | 10 | Registrar, needs access to bathroom facilities e.g. Staff Change Rooms
SHST | Shower - Staff, 3m2 | Yes | 1 | 3
SRM-15 | Staff Room, 15m2 | Yes | 1 | 30
SSTN | Staff Station, 20m2 | Yes | 1 | 25
CHST-10 | Change - Staff (Male / Female), 10m2 | Yes | 1 | 20 | Includes toilets, showers, lockers; size depends on the staffing per shift. (Female)
CHST-10 | Change - Staff (Male / Female), 10m2 | Yes | 1 | 20 | Includes toilets, showers, lockers; size depends on staffing per shift. (Male)
STFS-10 | Store- Files, 10m2 | Yes | 1 | 10
STPS-8 | Store - Photocopy / Stationery, 8m2 | Yes | 1 | 8
| Discounted Circulation % |  | 25%
SUPPORT AREAS
BBW | Bay - Blanket / Fluid Warming | Yes | 1 | 1 | Inclusion depends on operational policy of unit.
BHWS-A | Bay - Handwashing, Type A | Yes |  | 1 | Refer to Part D for numbers and locations
BMEQ-4 | Bay - Mobile Equipment, 4m2 | Yes | 3 | 4 | Locate in quiet low traffic areas.
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 4
BPATH | Bay - Pathology |  | 1 | 3 | Inclusion depends on operational policy of unit
BPTS | Bay - Pneumatic Tube |  | 1 | 1
CLRM-5 | Cleaner's Room, 5m2 | Yes | 1 | 5
CLUR-12 | Clean Utility, 12m2 | Yes | 2 | 12
DTUR-10 | Dirty Utility, 10m2 | Yes | 1 | 10
DISP-8 | Disposal Room, 8m2 | Yes | 1 | 8 | Inclusion depends on bed numbers and waste management guidelines. Preference for only 1 larger room.
CLUP-7 | Clean-Up Room, 7m2 | Yes | 1 | 18
| Respiratory / Biomedical Workroom |  | 1 | 20 | Inclusion depends on operational guidelines of unit.
STDR-10 | Medication Room, 10m2 | Yes | 1 | 10 | May be included with clean utility
STEQ-14 | Store - Equipment, 14m2 | Yes | 1 | 14 | General equipment
STEQ-20 | Store - Equipment, 20m2 | Yes |  |  | Inclusion depends on operational guidelines of unit. Required for storage of respiratory associated equipment and consumables.
STSS-30 | Store - Sterile Stock, 30m2 | Yes | 1 | 30
| Workroom - Telehealth |  | 1 | 12 | Optional: Inclusion depends on operational guideline of unit. Can be used for viewing medical images and discussions, and for telehealth activities for liaison regarding transfers, virtual rounds etc.
| Discounted Circulation % |  | 25%

## Level 3
Intensive Care General - Level 3
AusHFG Room Code | Room / Space | SC / SC-D | Qty | m2 | Remarks
ENTRY / RECEPTION
INTF | Interview Room | Yes | 1 | 12 | For interviews with relatives
MEET-12 | Meeting Room | Yes | 1 | 15 | For interviews with relatives.
WCPU-3 | Toilet - Public, 3m2 | Yes | 1 | 3
WAIT-10 | Waiting, 10m2 | Yes | 1 | 20 | Nominal area. To be calculated at 1.2m2 per able- bodied person, 1.5m2 per wheelchair occupant.
| Discounted Circulation % |  | 25%
PATIENT AREAS
PBC-24 | Patient Bay - Critical, 24m2 | Yes |  | 24 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
PBC-20 | Patient Bay - Critical, 20m2 | Yes |  | 20 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
PBCE-25 | Patient Bay - Critical (Enclosed), 20m2 | Yes |  | 25 | No. dependent on services planning; group of not more than 12, within easy observation of staff station.
| Patient Bay - Critical Enclosed (Class N Isolation) |  |  | 25 | No. dependent on services planning ; clustered, located away from Unit entrance.
ANRM | Anteroom | Yes |  | 6 | Attached to 1 Bed Rooms - Isolation Class N (neg pressure ventilation)
BATH | Bathroom | Yes | 1 | 15 | Inclusion depends on operational policy of unit
BLIN | Bay - Linen | Yes | 2 | 2
BRES | Bay - Resuscitation | Yes | 2 | 1.5
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 5
ENS-SP | Ensuite - Special, 6m2 | Yes | 1 | 1 x 6 | FPU; sizes for ‘full assistance’ i.e. 2 staff plus medical equipment.
| Discounted Circulation % |  | 40%
STAFF AREAS
MEET-L-20 | Meeting Room, 20m2 | Yes | 1 | 20 | Education / resource / teleheath - may include library, 24 hour access required via perimeter of unit.
MEET-L-30 | Meeting Room, 30m2 | Yes | 1 | 35 | Seminar / Training Room - alternative location for Library 24 hour access required; perimeter of unit.
OFF-CLW | Office – Clinical Workroom | Yes | 1 | 15 | Inclusion depends on operational policy of unit. Close to staff station
OFF-S9 | Office - Single Person, 9m2 | Yes |  | 9 | Senior Nurse Manager, NUM, staff specialists
OFF-S12 | Office - Single Person, 12m2 | Yes | 1 | 12 | Medical Director
| Office - Workstation, 4.4m2 |  |  | 4.4 | Registrars - workstation/s, open plan or enclosed. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | CNC/Educator-workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | Research - workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | Secretarial - workstation/s, open plan or in shared office. Number determined by staffing.
| Office - Workstation, 5.5m2 |  |  | 5.5 | General - workstation/s open plan or in shared office. Number determined by staffing.
OVBR | Overnight Stay - Bedroom | Yes | 1 | 10 | Registrar, needs access to bathroom facilities e.g. Staff Change Rooms
SHST | Shower - Staff, 3m2 | Yes | 1 | 3
SRM-15 | Staff Room, 15m2 | Yes | 1 | 35
SSTN | Staff Station, 20m2 | Yes | 2 | 25
CHST-10 | Change - Staff (Male / Female), 10m2 | Yes | 1 | 30 | Includes toilets, showers, lockers; size depends on the staffing per shift. (Female)
CHST-10 | Change - Staff (Male / Female), 10m2 | Yes | 1 | 25 | Includes toilets, showers, lockers; size depends on staffing per shift. (Male)
STFS-10 | Store- Files, 10m2 | Yes | 1 | 10
STPS-8 | Store - Photocopy / Stationery, 8m2 | Yes | 1 | 12
| Discounted Circulation % |  | 25%
SUPPORT AREAS
BBW | Bay - Blanket / Fluid Warming | Yes | 1 | 1 | Inclusion depends on operational policy of unit.
BHWS-A | Bay - Handwashing, Type A | Yes |  | 1 | Refer to Part D for numbers and locations
BMEQ-4 | Bay - Mobile Equipment, 4m2 | Yes | 3 | 4 | Locate in quiet low traffic areas.
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 | 4
BPATH | Bay - Pathology |  | 1 | 5 | Inclusion depends on operational policy of unit
BPTS | Bay - Pneumatic Tube |  | 1 | 1
CLRM-5 | Cleaner's Room, 5m2 | Yes | 1 | 5
CLUR-12 | Clean Utility, 12m2 | Yes | 2 | 12
DTUR-10 | Dirty Utility, 10m2 | Yes | 1 | 10
DISP-8 | Disposal Room, 8m2 | Yes | 2 | 8 | Inclusion depends on bed numbers and waste management guidelines. Preference for only 1 larger room.
CLUP-7 | Clean-Up Room, 7m2 | Yes | 1 | 18
| Respiratory / Biomedical Workroom |  | 1 | 20 | Inclusion depends on operational guidelines of unit.
STDR-10 | Medication Room, 10m2 | Yes | 1 | 10 | May be included with clean utility
STEQ-14 | Store - Equipment, 14m2 | Yes | 1 | 20 | General equipment
STEQ-20 | Store - Equipment, 20m2 | Yes | 1 | 20 | Inclusion depends on operational guidelines of unit. Required for storage of respiratory associated equipment and consumables.
STSS-30 | Store - Sterile Stock, 30m2 | Yes | 2 | 30
| Workroom - Telehealth |  | 1 | 12 | Optional: Inclusion depends on operational guideline of unit. Can be used for viewing medical images and discussions, and for telehealth activities for liaison regarding transfers, virtual rounds etc.
| Discounted Circulation % |  | 25%