## ICU SOA Rev. 7
ENTRY, WAITING & FAMILY SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | PICU - 14 beds |  | Adult ICU - 14 beds |  | Adult ICU - 56 beds (4 pods) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2
RECL-12 | Reception / Clerical | Yes | 1 | 10 (o) | 1 | 10 (o) | 1 | 12 | Optional. Provision will depend on the size of the unit and staffing arrangements.
WAIT-10 | Waiting | Yes | 1 | 15 | 1 | 15 | 1 | 40 | Nominal area. To be calculated at 1.2m2 per able- bodied person, 1.5m2 per wheelchair occupant.
PLAP-10 | Play Area - Paediatric | Yes | 1 | 10 (o) | Shared |  | 1 | 10 (o) | Optional.
BVM-3 | Bay - Vending Machine | Yes | 1 | 2 | 1 | 2 | 1 | 4 | Locate close to but not within waiting area given level of noise and heat generation.
BWD-1 | Bay - Water Dispenser | Yes | 1 | 1 | 1 | 1 | 1 | 1
BBEV-OP | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4
WCPU-3 | Toilet - Public | Yes | 1 | 3 | 1 | 3 | 4 | 3
WCAC | Toilet- Accessible | Yes | 1 | 6 (o) | 1 | 6 (o) | 1 | 6 (o) | Optional. Include if not located nearby.
PAR | Parenting Room | Yes | 1 | 6 (o) | 1 | 6 (o) | 1 | 6 (o) | Optional. Include if not located nearby.
INTF | Interview Room | Yes | 1 | 14 | 1 | 14 | 3 | 14 | For interviews with relatives. Include dual egress. Consider including some interview rooms within the clinical zone.
MEET-L-20 | Meeting Room | Yes | 1 | 20 (o) | 1 | 20 (o) | 1 | 20 | Multifunctional meeting room for family and staff meetings. Larger meeting room frequently required for end of life discussions.
OVBR | Overnight Stay - Bedroom | Yes | 2 | 10 | 1 | 10 | 3 | 10 | For families. Provision depends on local operational policies. May be designed for use during the day as overflow interview rooms
OVES | Overnight Stay - Ensuite | Yes | 2 | 4 | 1 | 4 | 3 | 4
PROP-2 | Property Bay | Yes | 1 | 1 (o) | 1 | 1 (o) | 1 | 2 (o) | Optional. For family / visitor belongings if using overnight stay rooms as multipurpose spaces.
| Discounted Circulation % |  |  | 25% |  | 25% |  | 25%
PATIENT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | PICU - 14 beds |  | Adult ICU - 14 beds |  | Adult ICU - 56 beds (4 pods) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2
1BR-IC | 1 Bed Room - Intensive Care | Yes | 7 | 25 | 13 | 25 | 50 | 25 | The number of enclosed vs open bays provided will depend on the patient cohort and infection control considerations. Includes provision for a palliative care space.
PBIC | Patient Bay - Intensive Care | Yes | 6 | 24.5 |  | 24.5 |  | 24.5
1BR-IC | 1 Bed Room - Intensive Care (Class N Isolation) | Yes | 1 | 25 | 1 | 25 | 4 | 25 | No. dependent on patient cohort and local jurisdictional policies.
1BR-IC | 1 Bed Room - Intensive Care (Class P Isolation) | Yes |  | 25 (o) |  | 25 (o) | 2 | 25 (o) | Optional. Depends on cohort and local jurisdictional requirements.
ANRM | Anteroom | Yes | 1 | 6 | 1 | 6 | 4 | 6 | Attached to 1 Bed Rooms - Isolation Class N (neg pressure ventilation).
BATH | Bathroom | Yes | 1 | 15 | 1 | 15 | 2 | 15 | Requires gases. May be shared between 2 pods subject to design.
ENS-SP | Ensuite - Special | Yes | 2 | 6 | 2 | 6 | 8 | 6 | Ensuites dedicated to negative pressure, positive pressure and standard isolation rooms. Number dependent on isolation room requirements. PICUs should include bathrooms with baths for younger children.
ENS-SP | Ensuite - Special | Yes | 3 | 6 | 3 | 6 | 12 | 6 | Ensuites to be shared between remaining rooms (1:4 ratio). PICUs should include bathrooms with baths for younger children.
SSTN-20 | Staff Station | Yes | 1 | 25 | 1 | 25 | 4 | 25 | 1 central staff station per pod.
OFF-CLN | Office – Clinical Workroom | Yes | 1 | 15 | 1 | 15 | 4 | 15 | 1 per pod.
| Decentralised Staff Workstation |  | 4 | 2 | 7 | 2 | 28 | 2 | 1 between 2 enclosed rooms.
BHWS-A | Bay - Handwashing, Type A | Yes | 2 | 1 | 2 | 1 | 8 | 1 | Also included within each patient bay.
BLIN | Bay - Linen | Yes | 1 | 2 | 1 | 2 | 4 | 2 | 1 per pod.
BRES | Bay - Resuscitation | Yes | 1 | 1.5 | 1 | 1.5 | 4 | 1.5 | 1 per pod.
BPATH | Bay - Pathology | Yes | 1 | 3 | 1 | 3 | 4 | 3 | 1 per pod. May be shared between 2 pods depending on layout.
BPTS | Bay - Pneumatic Tube | Yes | 1 | 1 | 1 | 1 | 4 | 1 | 1 per pod.
BMEQ-4 | Bay - Mobile Equipment | Yes | 3 | 4 | 3 | 4 | 12 | 4 | 3 per pod. Locate in quiet low traffic areas.
BBW | Bay - Blanket / Fluid Warming | Yes | 1 | 1 | 1 | 1 | 2 | 1 | Shared between 2 pods if collocated, subject to design.
| Discounted Circulation % |  |  | 40% |  | 40% |  | 40%
SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | PICU - 14 beds |  | Adult ICU - 14 beds |  | Adult ICU - 56 beds (4 pods) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2
BBEV-OP | Bay - Beverage, Open Plan | Yes | 1 | 4 | 1 | 4 | 2 | 4 | Share between 2 pods where collocated.
BMT-4 | Bay - Meal Trolley | Yes | 1 | 4 (o) | 1 | 4 (o) | 2 | 4 (o) | Optional. Depends on local operational policy for food services. Share between 2 pods where collocated.
| Formula Room |  | 1 | 9 |  |  |  |  | Used for formula preparation and storage, and sterilising of expressing equipment within PICUs.
STDR-10 | Medication Room | Yes | 1 | 12 | 1 | 12 | 2 | 20 | Share between 2 pods where collocated. Area to be distributed if automated dispensing units are provided centrally within central staff area.
| Store - Clean |  | 1 | 30 | 1 | 30 | 2 | 60 | Clean stock. Distribution between pods dependent on layout.
STEQ-20 | Store - Equipment | Yes | 1 | 28 | 1 | 28 | 1 | 112 | 2m2 per bed. May include specialty stores eg for retrieval equipment, renal, allied health etc.
STGN-9 | Store - General | Yes | 1 | 14 | 1 | 14 | 2 | 28
| Respiratory / Biomedical Workroom |  | 1 | 12 | 1 | 12 | 1 | 20 | For set up and servicing.
DTUR-12 | Dirty Utility | Yes | 1 | 12 | 1 | 12 | 4 | 12 | 1 per pod.
CLUP-7 | Clean-Up Room | Yes | 1 | 7 | 1 | 7 | 1 | 24
CLRM-5 | Cleaner's Room | Yes | 1 | 5 | 1 | 5 | 4 | 5 | Number and distribution depends on layout.
DISP-10 | Disposal Room | Yes | 1 | 8 | 1 | 8 | 1 | 20
| Simulation Room |  | 1 | 25 (o) |  |  | 1 | 25 (o) | Optional. Requirement will depend on education and training requirements / access to central simulation facilities.
| Simulation Control Room | [5 empty] | 1 | 10 (o) | Optional.
| Workroom - Telehealth |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 | Optional. Inclusion depends on operational guideline of unit. Can be used for viewing medical images and discussions, and for telehealth activities for liaison regarding transfers, virtual rounds etc.
WCST | Toilet - Staff | Yes | 2 | 3 | 2 | 3 | 6 | 3 | For ease of access from clinical areas.
| Discounted Circulation % |  |  | 40% |  | 40% |  | 40%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | PICU - 14 beds |  | Adult ICU - 14 beds |  | Adult ICU - 56 beds (4 pods) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2
OFF-S9 | Office - Single Person, 9m2 | Yes |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-S12 | Office - Single Person, 12m2 | Yes |  | 12 |  | 12 |  | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
| Office - Workstation, 4.4m2 |  |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
| Office - Workstation, 5.5m2 |  |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
MEET-L-15 | Meeting Room | Yes | 1 | 15 | 1 | 15 | 1 | 12
MEET-L-20 | Meeting Room | Yes | Shared |  | Shared |  | 1 | 20 | Assume shared access to 20m2 meeting room under Entry / Waiting & Family Support for smaller services.
MEET-L-55 | Meeting Room | Yes |  |  |  |  | 1 | 50
STPS-8 | Store - Photocopy / Stationery | Yes | 1 | 5 | 1 | 5 | 2 | 8
SRM-18 | Staff Room | Yes | 1 | 18 | 1 | 18 | 1 | 60
CHST-10 | Change - Staff (Male / Female) | Yes | 1 | 10 | 1 | 10 | 1 | 40 | Includes toilets, showers, lockers; size depends on the staffing per shift. (Female)
CHST-10 | Change - Staff (Male / Female) | Yes | 1 | 8 | 1 | 8 | 1 | 32 | Includes toilets, showers, lockers; size depends on staffing per shift. (Male)
WCAC | Toilet - Accessible | Yes | Shared |  | Shared |  | 1 | 6
OVBR | Overnight Stay - Bedroom | Yes | 1 | 10 (o) | 1 | 10 (o) | 1 | 10 (o) | Optional. Requirement depends on staffing arrangements. Close access to toilet / shower facilities required.
| Discounted Circulation % |  |  | 25% |  | 25% |  | 25%