## Entry_Reception
ENTRY / RECEPTION
AusHFG Room Code | Room / Space | SC / SC-D | Qty x m2 2 Cameras | Qty x m2 6 Cameras | Remarks
| Entry Lobby |  | 1 x 6 | 1 x 6
WAIT-10 | Waiting, 10m2 | Yes | 1 x 10 | 1 x 15
RECL-10 | Reception / Clerical, 10m2 | Yes | 1 x 10 | 1 x 15 | 1 and 2 staff
MEET-9 | Meeting Room, 9m2 | Yes | 1 x 9 | 1 x 9 | Private consultations, bookings etc
OFF-2P | Office - 2 Person, Shared, 12m2 | Yes | 1 x 12 | 1 x 15 | 2 & 3 staff
STPS-8 | Store - Photocopy / Stationery, 8m2 | Yes | 1 x 8 | 1 x 8
STFS-10 | Store - Files, 10m2 | Yes | 1 x 8 | 1 x 8
| Discounted Circulation |  | 25% | 30%

## Patient Care Area
PATIENT CARE AREA
AusHFG Room Code | Room / Space | SC / SC-D | Qty x m2 2 Cameras | Qty x m2 6 Cameras | Remarks
| Waiting - Dosed | Yes | 1 x 12 | 1 x 20 | Outpatients
| Waiting - Undosed | Yes | 1 x 6 | 1 x 9
PLAP-10 | Play Area - Paediatric, 10m2 | Yes | 1 x 10 (o) | 1 x 10 (o)
WCPT | Toilet - Patient, 4m2 | Yes | 2 x 4 | 2 x 4 | 1 male, 1 female
WCAC | Toilet - Accessible, 6m2 | Yes | 1 x 5 | 1 x 5
SHPT | Shower - Patient, 4m2 | Yes | 1 x 4 | 1 x 4 | For post-stress testing patient hygiene and incontinent patients
BBEV-OP | Bay - Beverage, Open Plan, 4m2 | Yes | 1 x 4 | 1 x 4
BWC | Bay - Wheelchair Park | Yes | 1 x 4 | 1 x 4 | May also include a patient trolley
| Entry Lobby - Inpatient |  | 1 x 6(o) | 1 x 6
PBTR-H-9 | Patient Bay - Holding, 9m2 | Yes | 3 x 9 | 8 x 9 | Curtained bays
BHWS-B | Bay - Handwashing, Type B | Yes | 1 x 1 | 2 x 1 | Part of Inpatient Holding Area
| Staff Station / Clean Utility |  | 1 x 8 | 1 x 10 | Part of Inpatient Holding Area
BLIN | Bay - Linen | Yes | 1 x 2 | 1 x 2 | Part of Inpatient Holding Area
STSS-12 | Store - Sterile Stock, 12m2 | Yes * | 1 x 10 | 1 x 12
DTUR-S | Dirty Utility - Sub, 8m2 | Yes | 1 x 8 | 1 x 8
DISP-8 | Disposal Room, 8m2 | Yes | 1 x 8 | 1 x 8
| Discounted Circulation |  | 32% | 35%

## Treatment Areas
TREATMENT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | Qty x m2 2 Cameras | Qty x m2 6 Cameras | Remarks
| SPECT Scanning Room (Inlcudes Control Bay) |  | 42 | 42 | Rooms should be rectangular (e.g. 6x7m)
| SPECT / CT Scanning Room |  | 48 | 48 | Rooms should be rectangular (e.g. 6x8m)
| SPECT Control Room |  | 10 | 10
BMEQ-4 | Bay - Mobile Equipment, 4m2 | Yes | 1 x 4 | 2 x 4
BMEQ-4 | Bay - Mobile Equipment, 4m2 | Yes | 1 x 2 | 1 x 2 | Technegas machine & argon cylinder
STRT | Stress Test Room | Yes | 1 x 16 | 1 x 16 | Add 2m2 if includes resuscitation trolley
BRES | Bay - Resuscitation | Yes | 1 x 1.5 | 1 x 1.5 | Unless located in Stress Testing Room
CONS | Consult Room | Yes | 2 x 12 | 4 x 12 | For dose administration and examination. Radiation safety advice may be required.
TRMT | Treatment Room | Yes |  | 1 x 14 (o) | Ideally adjacent to the Hot / Dispensing Lab
| Bone Density Measurement Room | Yes | 1 x 12 (o) | 1 x 12 (o) | Increase to 16m2 if trolley / bed access required
STEQ-14 | Store - Equipment, 14m2 | Yes | 1 x 9 | 1 x 12
| Computer Room |  | 1 x 8 | 1 x 8 | Computers, printer
XRRR | X-Ray Viewing & Reporting Room | Yes | 1 x 10 | 1 x 25 | 2 & 5 workstations near scanning rooms
| Discounted Circulation |  | 35% | 35%

## Hot Laboratory
HOT LABORATORY
AusHFG Room Code | Room / Space | SC / SC-D | Qty x m2 2 Cameras | Qty x m2 6 Cameras | Remarks
| Entry Lobby - Isotope Delivery |  | 1 x 4 (o) | 1 x 4 (o) | delivered directly into unit. May be combined with Waste Holding Store
| Hot Lab / Therapy Dispensing |  | 1 x 10 | 1 x 12 | Fume hood, dose calibrator, balance, centrifuge etc
| Radioactive Waste Holding Store |  | 1 x 4 | 1 x 6
BES | Bay - Emergency Shower | Yes | 1 x 2 | 1 x 2 | Decontamination
| Discounted Circulation |  | 15% | 15%

## Staff Areas
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | Qty x m2 2 Cameras | Qty x m2 6 Cameras | Remarks
OFF-S12 | Office - Single Person, 12m2 | Y | 1 x 12 | 1 x 12 | Unit director
| Office - Workstation, 5.5m2 |  | 1 x 5.5 (o) | 1 x 5.5 | Secretary to Director
OFF-S9 | Office - Single Person, 9m2 | Y | 9 | 9 | Number depends on staff establishment. Staff Specialists.
| Office - Workstation, 5.5m2 |  | 5.5 | 5.5 | Number depends on staff establishment. Registrars.
OFF-S9 | Office - Single Person, 12m2 | Y | 1 x 9 (o) | 1 x 12 | Chief Physicist.
| Office - Workstation, 5.5m2 |  | 5.5 (o) | 5.5 | Number depends on staff establishment. Physicists.
| Office - Single Person, 9m2 | Y | 1 x 9 (o) | 1 x 9 | Chief Technologist, Radiopharmacist, NUM.
| Office - Workstation, 5.5m2 |  | 5.5 | 5.5 | Number depends on staff establishment. Technologists.
| Office - Workstation, 5.5m2 |  | 5.5 | 5.5 | Number depends on staff establishment. Medical Typists.
SRM-15 | Staff Room | Y | 1 x 15 | 1 x 25 | Includes beverage bay
MEET-12 | Meeting Room, 12m2 | Y | 1 x 12 | 2 x 12
PROP-2 | Property Bay - Staff | Y | 1 x 2 | 2 x 2 | Size depends on staff establishment
SHST | Shower - Staff, 3m2 | Y | 1 x 3 | 1 x 3
WCST | Toilet - Staff, 3m2 | Y | 2 x 3 | 2 x 3 | *Number will depend on staff establishment
CLRM-5 | Cleaner's Room, 5m2 | Y | 1 x 5 | 1 x 5 | *May be shared with adjoining unit
| Discounted Circulation |  | 25% | 30%