## Revision 7.1(MM) (hidden)
HPU 540 Paediatric / Adolescent Unit - Schedule of Accommodation, Revision 7
AMBULATORY CARE - ENTRY / RECEPTION / WAITING
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 2 Rooms |  | 5 Rooms + 2 Medical Day Spaces |  | 7 Rooms + 4 Medical Day Spaces
|  |  | Qty | m2 | Qty | m2 | Qty | m2
ENTRY
RECL-10 | Reception | Yes | Shared with IPU |  | 1 | 10 (o) | 1 | 10 (o) | Optional. Where ambulatory and inpatient services are collocated, a single reception may be provided. A dedicated reception will not routinely be provided to a stand-alone inpatient unit owing to recurrent cost implications.
WAIT-10 | Waiting | Yes | Shared with IPU |  | 1 | 10 | 1 | 15 | Area recommendation is indicative in size and is dependant on the size of the ambulatory care service. 1.2m2 recommended per seat, 1.5m2 per wheelchair space.
PLAY | Play Area - Paediatric | Yes |  |  | 1 | 8 | 1 | 10
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 (o) | Optional. To be included if not located nearby.
WCPU | Toilet - Public | Yes | Shared |  | 1 | 3 (o) | 1 | 3 (o) | Optional. To be included if not located nearby. Number of toilets to align with BCA requirement.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. To be included if one not located nearby.
| Discounted Circulation |  | 32% |  | 32% |  | 32% |  | Note: circulation allowance will vary depending on the scale and complexity of the service
AMBULATORY CARE - PATIENT AREAS
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 2 Rooms |  | 5 Rooms + 2 Medical Day Spaces |  | 7 Rooms + 4 Medical Day Spaces
|  |  | Qty | m2 | Qty | m2 | Qty | m2
PBTR-H-9 | Patient Bay - Holding | Yes |  |  | 1 | 9 | 3 | 9 | Assessment/ Day Stay. May be used for short term holding of children and/ or for day stay procedures.
| 1 Bed Room - Holding |  |  |  | 1 | 15 (o) | 1 | 15 | Similar to PBTR-H-9 but enclosed and includes a handwash basin. Optional for scenario 2. A standard isolation room to manage conditions such as gastroenteritis or oncology cases. Assumes day-only care.
ENS-ST-A1 ENS-ST-A2 ENS-ST-A3 ENS-ST-B ENS-ST-C | Ensuite - Inboard | Yes |  |  | 1* | 5 | 2 | 5 | * In Scenario 2, if the optional 1 Bed Room is adopted, add a second ensuite. May be provided as alternative ensuite arrangement ENS-ST-A1, ENS-ST-A2, ENS-ST-A3, ENS-ST-B or ENS-ST-C.
CONS | Consult Room | Yes | 1 | 14 (o) | 3 | 14 | 5 | 14 | Optional size for scenario 1. Larger size to accommodate prams and siblings. Number of rooms will be dependent on anticipated occasions of service. For larger units consider a mix of universal (17m2) and standard (14m2) consult rooms.
CONS-UN | Consult room - Universal Access | Yes | 1 | 17 (o) | 1 | 17 | 1 | 17 | Optional size for scenario 1. Number of rooms will be dependent on anticipated occasions of service. For larger units consider a mix of universal and standard consult rooms.
INTV | Interview Room | Yes |  |  | 1 | 12 (o) | 1 | 12 (o) | Optional
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 4
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1
DTUR-S | Dirty Utility, Sub | Yes | Shared |  | 1 | 8 (o)* | 1 | 8 | Optional for scenario 2. Size of Dirty Utility is dependent on the scope of services provided in the Ambulatory Care unit. *May be shared with adjacent inpatient unit
SSTN-10 | Staff Station | Yes |  |  | 1 | 10 (o)* | 1 | 10 | Optional for scenario 2. * for smaller units may be shared with adjacent inpatient unit.
CLN-10 | Clean Store | Yes |  |  | 1 | 5 (o)* | 1 | 10 | Optional for scenario 2. For storage of consumables used in the Ambulatory Care unit. * for smaller units may be shared with adjacent inpatient unit.
| Discounted Circulation |  | 32% |  | 32% |  | 32% |  | Note: circulation allowance will vary depending on the scale and complexity of the service
INPATIENT AREAS
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
1BR-ST-A1 1BR-ST-A2 1BR-ST-A3 1BR-ST-B1 1BR-ST-B2 1BR-ST-B3 1BR-ST-D | 1 Bed Room | Yes | 3 | 18 | 7 | 18 | 15 | 18 | Bed/chair for parent. Provision for a 20m2 maybe required to accommodate additional equipment or additional staff/ services for children presenting with mental health conditions. If using an 8,400mm structural grid refer to 1BR-ST-A2,1BR-ST-A3 (both with inboard ensuite), 1BR-ST-B2 or 1BR-ST-B3 (both with outboard ensuite) or 1BR-ST-D (back to back ensuite). For 1 Bed Rooms on a 7,800mm structural grid, refer to 1BR-ST-A1 or 1BR-ST-B1.
1BR-IS-N1 1BR-IS-N2 | 1 Bed Room - Isolation Negative Pressure | Yes | 1 | 18 | 1 | 18 | 1 | 18 | Bed/chair for parent. Class N Isolation Rooms
ANRM | Anteroom | Yes | 1 | 6 | 1 | 6 | 1 | 6 | For Class N Isolation Rooms
2BR-ST-A1 2BR-ST-A2 | 2 Bed Room | Yes | 1 | 31 | 2 | 31 | 4 | 31 | For older children
ENS-ST-A1 ENS-ST-A2 ENS-ST-A3 ENS-ST-B ENS-ST-C | Ensuite | Yes | 4 | 5 | 9 | 5 | 19 | 5 | May be provided as alternative ensuite arrangement ENS-ST-A1, ENS-ST-A2, ENS-ST-A3, ENS-ST-B or ENS-ST-C.
ENS-ACC | Ensuite - Accessible | Yes | 1 | 7 | 1 | 7 | 1 | 7 | Consideration of the patient cohort is required regarding the number of accessible ensuites required.
BHWS-B | Bay - Handwashing - Type B | Yes | 1 | 1 | 2 | 1 | 4 | 1
| Discounted Circulation |  | 32% |  | 35% |  | 38% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.
INPATIENT AREAS - CHILD SPECIFIC SPACE
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
| Play Room |  | 1 | 12 (o) | 1 | 20 | 1 | 35 | This room may a.lso be used by Play Therapist. Opportunity to share with adjacent unit depending on patient cohorts.
| Discounted Circulation |  | 32% |  | 35% |  | 38%
INPATIENT AREAS - ADOLESCENT SPECIFIC SPACE
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
| Recreation Room |  | 1 | 14 (o) | 1 | 25 (o) | 1 | 35 (o) | Computers, patient entertainment systems, music etc. Optional beverage bay.
| Quiet Study Room |  | 1 | 9 (o) | 1 | 12 (o) | 1 | 15 (o)
| Discounted Circulation |  | 32% |  | 35% |  | 38% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.
CLINICAL SUPPORT AREAS
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
| Bathroom - Paediatric |  | 1 | 16 (o) | 1 | 16 | 1 | 16 | Include a baby bath, change table and low-set toilet for toddlers.
BLIN | Bay - Linen | Yes | 1 | 2 | 1* | 2 | 2 | 2 | Typically enclosed in Paediatric Units. For scenario 2, assumes 2 linen bays in total with 1 bay in collocated Ambulatory Care
BRES | Bay - Resuscitation Trolley | Yes | Shared |  | 2 | 1.5 | 2 | 1.5 | Assumes one for infants, one for adolescents. Assumes one bay for resuscitation trolley and one bay for infant resuscitation & warming device. Secure location needed.
BPTS | Bay - Pneumatic Tube Station | Yes | Shared |  | 1 | 1 | 1 | 1
PTRY | Pantry | Yes | Shared |  | 1 | 8 | 1 | 8 | This room will also be used to store snacks for children and adolescents.
BMT-4 | Bay – Meal Trolley | Yes | Shared |  | 1 | 4 | 1 | 4
BMEQ | Bay – Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | For storage of items including workstation on wheels, teleconferencing equipment and observation machines.
| Milk Preparation & Storage |  | Shared |  | 1 | 6 (o) | 1 | 10 | May be located in Maternity Unit in scenario 1. Includes storage of powdered formula, refrigerated ready-made formula and secure refrigerated storage for EBM. Assumes single use items for breast pump accessories and bottles. Refer to 4.2.8 for further information.
SSTN-14 | Staff Station | Yes | Shared |  | 1 | 14 | 2* | 12 | May be provided as one larger staff station
OFF-CLN | Office - Clinical Workroom | Yes | Shared |  | 1 | 12 | 1 | 15
BMFD-3 | Bay - Multifunction Device | Yes | Shared |  | 1 | 3 | 1 | 7 | May be collocated with offices.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room based on local jurisdictional policies.
MED-14 | Medication Room | Yes | Shared |  | 1 | 14 | 1 | 14 | May be provided as a combined Clean Store / Medication Room based on local jurisdictional policies. Larger room may be required for scenario 3 depending on staff numbers.
PROC | Procedure Room - Paediatrics | Yes | Shared |  | 1 | 16 | 1 | 20 | Procedure Room is used for carrying out procedures away from the patient bedside. For further information refer to notes in 4.2.4. Larger size Procedure Room may be required depending on types of procedures.
DTUR-12 DTUR-14 | Dirty Utility | Yes | Shared |  | 1 | 12 | 1 | 14 | May need 2 rooms depending on IPU layout.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 10 | 1 | 10 | Disposal Room may be shared with adjacent unit. Size will be dependent on local waste management policies.
INTV | Interview Room | Yes | Shared |  | 1 | 12 | 1 | 12 | May also be used as a quiet space for breastfeeding.
| Therapy / Multipurpose Room |  |  |  | 1 | 20 | 1 | 20
STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 20 | 1 | 30 | For storage of items such as strollers, highchairs, breast pumps and other general & medical equipment
STEQ-20 | Store - Equipment | Yes | 1 | 12 | 1 | 20 | 1 | 20 | Includes storage for beds and cots
STGN | Store – General | Yes | Shared |  | 1 | 9 | 1 | 9 | Clinical Consumables
CLRM-5 | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | May be shared with adjacent unit in 12 and 24 bed scenarios.
| Lounge - Parent | Yes | 1 | 10 (o) | 1 | 16 | 1 | 22 | May include sofa bed. Space for caregiver to relax and eat meals away from the bedside. Room size dependent on patient cohorts.
BBEV-OP | Bay - Beverage, Open Plan | Yes |  |  | 1 | 4 | 1 | 4 | Collocate with Parent Lounge.
OVES | Overnight Stay - Ensuite | Yes |  |  | 1 | 5 | 1 | 5 | Provided for caregivers.
LAUN-PT | Laundry | Yes |  |  | 1 | 6 (o) | 1 | 6 (o) | Optional. For use by caregivers if cohorts include longer term patients.
| Discounted Circulation |  | 32% |  | 35% |  | 38% |  | Note: circulation allowance will vary depending on the scale and complexity of the service
STAFF AREAS
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
OFF-1P-12 | Office - 1 Person, 12m2 | Yes |  |  |  | 12 |  | 12 | Number and area allocation will depend on staff profile and local jurisdictional policies.
OFF-1P-9 | Office - 1 Person, 9m2 | Yes |  | 9 |  | 9 |  | 9
OFF-2P | Office - 2 Person | Yes |  |  |  | 12 |  | 12
OFF-WS | Office - Workstation | Yes |  | 4.5 |  | 4.5 |  | 4.5
MEET-20 | Meeting Room | Yes | Shared |  | 1 | 18 | 1 | 20
SRM-15 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 18 | Number and area allocation will depend on staff profile and local jurisdictional policies.
BPROP | Bay - Property, Staff | Yes | Shared |  | 1 | 2 | 1 | 3 | Number and area allocation will depend on staff profile and local jurisdictional policies.
WCST | Toilet - Staff | Yes | Shared |  | 2 | 3 | 2 | 3 | Number and area allocation will depend on staff profile and local jurisdictional policies.
SHST | Shower - Staff | Yes | Shared |  | 1 | 3 (o) | 1 | 3 (o) | Optional
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.

## Revision 7
HPU 540 Paediatric / Adolescent Unit - Schedule of Accommodation, Revision 7
AMBULATORY CARE - ENTRY / RECEPTION / WAITING
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 2 Rooms |  | 5 Rooms + 2 Medical Day Spaces |  | 7 Rooms + 4 Medical Day Spaces
|  |  | Qty | m2 | Qty | m2 | Qty | m2
RECL-10 | Reception | Yes | Shared with IPU |  | 1 | 10 (o) | 1 | 10 (o) | Optional. Where ambulatory and inpatient services are collocated, a single reception may be provided. A dedicated reception will not routinely be provided to a stand-alone inpatient unit owing to recurrent cost implications.
WAIT-10 | Waiting | Yes | Shared with IPU |  | 1 | 10 | 1 | 15 | Area recommendation is indicative in size and is dependant on the size of the ambulatory care service. 1.2m2 recommended per seat, 1.5m2 per wheelchair space.
PLAY | Play Area - Paediatric | Yes |  |  | 1 | 8 | 1 | 10
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 (o) | Optional. To be included if not located nearby.
WCPU | Toilet - Public | Yes | Shared |  | 1 | 3 (o) | 1 | 3 (o) | Optional. To be included if not located nearby. Number of toilets to align with BCA requirement.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. To be included if one not located nearby.
| Discounted Circulation |  | 32% |  | 32% |  | 32% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.
AMBULATORY CARE - PATIENT AREAS
| Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 2 Rooms |  | 5 Rooms + 2 Medical Day Spaces |  | 7 Rooms + 4 Medical Day Spaces
|  |  | Qty | m2 | Qty | m2 | Qty | m2
PBTR-H-9 | Patient Bay - Holding | Yes |  |  | 1 | 9 | 3 | 9 | Assessment/ Day Stay. May be used for short term holding of children and / or for day stay procedures.
| 1 Bed Room - Holding |  |  |  | 1 | 15 (o) | 1 | 15 | Similar to PBTR-H-9 but enclosed and includes a handwash basin. Optional for scenario 2. A standard isolation room to manage conditions such as gastroenteritis or oncology cases. Assumes day-only care.
ENS-ST-A1 ENS-ST-A2 ENS-ST-A3 ENS-ST-B ENS-ST-C | Ensuite - Inboard | Yes |  |  | 1* | 5 | 2 | 5 | * In Scenario 2, if the optional 1 Bed Room is adopted, add a second ensuite. May be provided as alternative ensuite arrangement ENS-ST-A1, ENS-ST-A2, ENS-ST-A3, ENS-ST-B or ENS-ST-C.
CONS | Consult Room | Yes | 1 | 14 (o) | 3 | 14 | 5 | 14 | Optional size for scenario 1. Larger size to accommodate prams and siblings. Number of rooms will be dependent on anticipated occasions of service. For larger units consider a mix of universal (17m2) and standard (14m2) consult rooms.
CONS-UN | Consult room - Universal Access | Yes | 1 | 17 (o) | 1 | 17 | 1 | 17 | Optional size for scenario 1. Number of rooms will be dependent on anticipated occasions of service. For larger units consider a mix of universal and standard consult rooms.
INTV | Interview Room | Yes |  |  | 1 | 12 (o) | 1 | 12 (o) | Optional
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | Typically enclosed in Paediatric Units.
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 4
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1
DTUR-S | Dirty Utility, Sub | Yes | Shared |  | 1 | 8 (o)* | 1 | 8 | Optional for scenario 2. Size of Dirty Utility is dependent on the scope of services provided in the Ambulatory Care unit. *May be shared with adjacent inpatient unit.
SSTN-10 | Staff Station | Yes |  |  | 1 | 10 (o)* | 1 | 10 | Optional for scenario 2. * for smaller units may be shared with adjacent inpatient unit.
CLN-10 | Clean Store | Yes |  |  | 1 | 5 (o)* | 1 | 10 | Optional for scenario 2. For storage of consumables used in the Ambulatory Care unit. * for smaller units may be shared with adjacent inpatient unit.
| Discounted Circulation |  | 32% |  | 32% |  | 32% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.
INPATIENT AREAS
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
1BR-ST-A1 1BR-ST-A2 1BR-ST-A3 1BR-ST-B1 1BR-ST-B2 1BR-ST-B3 1BR-ST-D | 1 Bed Room | Yes | 3 | 18 | 7 | 18 | 15 | 18 | Bed / chair for parent. Provision for a 20m2 maybe required to accommodate additional equipment or additional staff / services for children presenting with mental health conditions. If using an 8,400mm structural grid refer to 1BR-ST-A2,1BR-ST-A3 (both with inboard ensuite), 1BR-ST-B2 or 1BR-ST-B3 (both with outboard ensuite) or 1BR-ST-D (back to back ensuite). For 1 Bed Rooms on a 7,800mm structural grid, refer to 1BR-ST-A1 or 1BR-ST-B1.
1BR-IS-N1 1BR-IS-N2 | 1 Bed Room - Isolation Negative Pressure | Yes | 1 | 18 | 1 | 18 | 1 | 18 | Bed/chair for parent. Class N Isolation Rooms
ANRM | Anteroom | Yes | 1 | 6 | 1 | 6 | 1 | 6 | For Class N Isolation Rooms
2BR-ST-A1 2BR-ST-A2 | 2 Bed Room | Yes | 1 | 31 | 2 | 31 | 4 | 31 | For older children
ENS-ST-A1 ENS-ST-A2 ENS-ST-A3 ENS-ST-B ENS-ST-C | Ensuite | Yes | 4 | 5 | 9 | 5 | 19 | 5 | May be provided as alternative ensuite arrangement ENS-ST-A1, ENS-ST-A2, ENS-ST-A3, ENS-ST-B or ENS-ST-C.
ENS-ACC | Ensuite - Accessible | Yes | 1 | 7 | 1 | 7 | 1 | 7 | Consideration of the patient cohort is required regarding the number of accessible ensuites required.
BHWS-B | Bay - Handwashing - Type B | Yes | 1 | 1 | 2 | 1 | 4 | 1
| Discounted Circulation |  | 32% |  | 35% |  | 38% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.
INPATIENT AREAS - CHILD SPECIFIC SPACE
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
| Play Room |  | 1 | 12 (o) | 1 | 20 | 1 | 35 | This room may also be used by Play Therapist. Consider opportunity to share with adjacent unit. Room size dependent on patient cohorts.
| Discounted Circulation |  | 32% |  | 35% |  | 38%
INPATIENT AREAS - ADOLESCENT SPECIFIC SPACE
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
| Recreation Room |  | 1 | 14 (o) | 1 | 25 (o) | 1 | 35 (o) | Computers, patient entertainment systems, music etc. Optional beverage bay.
| Quiet Study Room |  | 1 | 9 (o) | 1 | 12 (o) | 1 | 15 (o)
| Discounted Circulation |  | 32% |  | 35% |  | 38% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.
CLINICAL SUPPORT AREAS
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
| Bathroom - Paediatric |  | 1 | 16 (o) | 1 | 16 | 1 | 16 | Include a baby bath, change table and low-set toilet for toddlers.
BLIN | Bay - Linen | Yes | 1 | 2 | 1* | 2 | 2 | 2 | Typically enclosed in Paediatric Units. For scenario 2, assumes 2 linen bays in total with 1 bay in collocated Ambulatory Care.
BRES | Bay - Resuscitation Trolley | Yes | Shared |  | 2 | 1.5 | 2 | 1.5 | Assumes one bay for resuscitation trolley and one bay for infant resuscitation & warming device. Lockable resuscitation trolley preferred. Secure location needed.
BPTS | Bay - Pneumatic Tube Station | Yes | Shared |  | 1 | 1 | 1 | 1
PTRY | Pantry | Yes | Shared |  | 1 | 8 | 1 | 8 | This room will also be used to store snacks for children and adolescents.
BMT-4 | Bay – Meal Trolley | Yes | Shared |  | 1 | 4 | 1 | 4
BMEQ | Bay – Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | For storage of items including workstation on wheels, teleconferencing equipment and observation machines.
| Milk Preparation & Storage |  | Shared |  | 1 | 6 (o) | 1 | 10 | May be located in Maternity Unit in scenario 1. Includes storage of powdered formula, refrigerated ready-made formula and secure refrigerated storage for EBM. Assumes single use items for breast pump accessories and bottles. Refer to 4.2.8 for further information.
SSTN-14 | Staff Station | Yes | Shared |  | 1 | 14 | 2* | 12 | May be provided as one larger staff station.
OFF-CLN | Office - Clinical Workroom | Yes | Shared |  | 1 | 12 | 1 | 15
BMFD-3 | Bay - Multifunction Device | Yes | Shared |  | 1 | 3 | 1 | 7 | May be collocated with offices.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room based on local jurisdictional policies.
MED-14 | Medication Room | Yes | Shared |  | 1 | 12 | 1 | 14 | May be provided as a combined Clean Store / Medication Room based on local jurisdictional policies. Larger room may be required for scenario 3 depending on staff numbers.
PROC | Procedure Room - Paediatrics | Yes | Shared |  | 1 | 16 | 1 | 20 | Procedure Room is used for carrying out procedures away from the patient bedside. For further information refer to notes in 4.2.4. Larger size Procedure Room may be required depending on types of procedures.
DTUR-12 DTUR-14 | Dirty Utility | Yes | Shared |  | 1 | 12 | 1 | 14 | May need 2 rooms depending on IPU layout.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 10 | 1 | 10 | Disposal Room may be shared with adjacent unit. Size will be dependent on local waste management policies.
INTV | Interview Room | Yes | Shared |  | 1 | 12 | 1 | 12 | May also be used as a quiet space for breastfeeding.
| Therapy / Multipurpose Room |  |  |  | 1 | 20 | 1 | 20
STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 20 | 1 | 30 | For storage of items such as strollers, highchairs, breast pumps and other general & medical equipment.
STEQ-20 | Store - Equipment | Yes | 1 | 12 | 1 | 20 | 1 | 20 | Includes storage for beds and cots
STGN | Store - General | Yes | Shared |  | 1 | 9 | 1 | 9 | Clinical Consumables
CLRM-5 | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | May be shared with adjacent unit in 12 and 24 bed scenarios.
| Family Lounge | Yes | 1 | 10 (o) | 1 | 16 | 1 | 22 | May include sofa bed. Space for caregiver to relax and eat meals away from the bedside. Room size dependent on patient cohorts.
BBEV-OP | Bay - Beverage, Open Plan | Yes |  |  | 1 | 4 | 1 | 4 | Collocate with Family Lounge.
OVES | Overnight Stay - Ensuite | Yes |  |  | 1 | 5 | 1 | 5 | Provided for caregivers.
LAUN-PT | Laundry | Yes |  |  | 1 | 6 (o) | 1 | 6 (o) | Optional. For use by caregivers if cohorts include longer term patients.
| Discounted Circulation |  | 32% |  | 35% |  | 38% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.
STAFF AREAS
Room Code | Room / Space | SC / SC-D | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Remarks
|  |  | 6 beds |  | 12 beds |  | 24 beds
|  |  | Qty | m2 | Qty | m2 | Qty | m2
OFF-1P-12 | Office - 1 Person, 12m2 | Yes |  |  |  | 12 |  | 12 | Number and area allocation will depend on staff profile and local jurisdictional policies.
OFF-1P-9 | Office - 1 Person, 9m2 | Yes |  | 9 |  | 9 |  | 9
OFF-2P | Office - 2 Person | Yes |  |  |  | 12 |  | 12
OFF-WS | Office - Workstation | Yes |  | 4.5 |  | 4.5 |  | 4.5
MEET-20 | Meeting Room | Yes | Shared |  | 1 | 18 | 1 | 20
SRM-15 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 18 | Number and area allocation will depend on staff profile and local jurisdictional policies.
BPROP | Bay - Property, Staff | Yes | Shared |  | 1 | 2 | 1 | 3 | Number and area allocation will depend on staff profile and local jurisdictional policies.
WCST | Toilet - Staff | Yes | Shared |  | 2 | 3 | 2 | 3 | Number and area allocation will depend on staff profile and local jurisdictional policies.
SHST | Shower - Staff | Yes | Shared |  | 1 | 3 (o) | 1 | 3 (o) | Optional
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | Note: circulation allowance will vary depending on the scale and complexity of the service.