## ED SOA Rev 7
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 5 bays (Acute + Fast Track) |  | 15 bays (Acute + Fast Track) |  | 30 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 10 | 1 | 10 | 1 | 10 | Offset doors
WAIT-20 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6 | Accessible from waiting areas.
BPH | Bay - Public Telephone | Yes | Shared |  | 1 | 2 (o) | 1 | 2 (o) | 1 | 2 (o)
BVM-3 | Bay - Vending Machines | Yes | Shared |  | 1 | 3 (o) | 1 | 3 | 2 | 3
BWD-1 | Bay - Water Dispenser | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU-3 | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 5 bays (Acute + Fast Track) |  | 15 bays (Acute + Fast Track) |  | 30 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
REC-E | Reception, Emergency | Y | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated.
TRIAGE -1/2 | Triage Assessment Room, Emergency |  | Shared |  | 1 | 13 | 2 | 13 | 3 | 13 | No. dependent on operational arrangements.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ-6 | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/ trolley hold
OFF-S9 | Office - Single Person | Yes |  |  | 1 | 9 | 1 | 9 | 1 | 9 | NUM / Front of House coordinator. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | To be located in a non public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 5 bays (Acute + Fast Track) |  | 15 bays (Acute + Fast Track) |  | 30 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for waste water detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency -Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 8 | Ambulance service write up. 2 write up spaces within 5m2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV-OP | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ-4 | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUS
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 1 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 1 | 25 | 3 | 25 | 4 | 25 | Number of resus bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resucitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment/Resuscitation |  | 1 | 16
BMEQ-4 | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
CLUR-12 | Clean Utility / Medication Room | Yes | Shared |  | Shared |  | 1 | 12 | 1 | 14 | Includes small medication store with fridge and drug safe, to be shared between resuscitation bays.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | For staff to meet with family and friends of patients. Also used as a quiet/ grieving space. Number will depend on size of service. Also refer to allocation in acute zone below.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 5 bays (Adults + Paeds) |  | 10 Acute Bays (Adults + Paeds) |  | 14 Adult Acute Bays |  | 30 Adult Acute Bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 5 | 12 | 8 | 12 | 10 | 12 | 25 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N isolation | Yes |  |  |  |  | 1 | 15 | 1 | 15 | Negative pressure isolation.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  | 2 | 5 | 3 | 5 | 4 | 5 | Dedicated to each Class N and Class S room
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite - Standard | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room, Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes |  |  | 2 | 4 | 2 | 4 | 4 | 4
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 3 | 4
SHD | Shower - Accessible |  | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
CLUR-12 | Clean Utility / Medication Room | Yes | Shared |  | 1 | 10 | 1 | 12 | 2 | 12 | Include medication store where not provided separately.
STDR-10 | Medication Room | Yes | Shared |  |  |  | 1 | 10 | 1 | 10
BHWS-B | Bay - Handwashing,Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ-4 | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV-OP | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 15 Paediatric Acute Bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 11 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
CLUR-12 | Clean Utility / Medication Room | Yes |  |  |  |  | 1 | 8 | 1 | 12
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ-4 | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV-OP | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 5 Fast Track Spaces |  | 10 Fast Track Spaces |  | 15 Fast Track Spaces
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 3 | 6.5 | 7 | 6.5 | 10 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 | 12 | 5 | 12 | The mix of bays and consult rooms will be dependent on project requirements.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16
| Consult - Dental | [5 empty] | 1 | 12(o) | 1 | 12(o) | Determined by need/ activity. A knee break chair might be included to increase flexibility.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 | 1 | 14
| Store - Crutch | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ-4 | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
SUPPORT
AusHFG Room Code | Room / Space | SC / SC-D | 5 bays (Acute + Fast Track) |  | 15 bays (Acute + Fast Track) |  | 30 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN-9 | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs
STEQ-14 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster managament role.
DISP-8 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service.
CLRM-5 | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 2 | 3 | For close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 6 bays |  | 12 bays |  | 20 bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 6 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite - Standard | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashin, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
CLUR-12 | Clean Utility / Medication Room | Yes |  |  | 1 | 10 (o) | 1 | 12 | 1 | 14
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM-5 | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV-OP | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT-4 | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 5 bays |  | 15 bays |  | 30 bays |  | 60 bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
SRM-15 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30
CHST-20 | Change - Staff (Male/Female) | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere
PROP-2 | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-S12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-S9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
| Office - Workstation |  |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
| Office - Workstation |  |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
STPS-8 | Store - Photocopy/ Stationery | Yes | Shared |  | 1 | 8 | 1 | 8 | 1 | 8
MEET-L-20 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-12 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%