## ED SOA Rev 8 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 5 6 bays (Acute + Fast Track) |  | 15 18 bays (Acute + Fast Track) |  | 30 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 10 | 1 | 10 | 1 | 10 | Offset doors
WAIT-20 WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6 | Accessible from waiting areas.
BPH | Bay - Public Telephone | Yes | Shared |  | 1 | 2 (o) | 1 | 2 (o) | 1 | 2 (o)
BVM-3 BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 3 2 (o) | 1 | 3 2 | 2 | 3 2
BWD-1 BWTR | Bay - Water Dispenser Fountain | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU-3 WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 5 6 bays (Acute + Fast Track) |  | 15 18 bays (Acute + Fast Track) |  | 30 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated.
TRIAGE -1/2 | Triage Assessment Room, Emergency |  | Shared |  | 1 | 13 | 2 | 13 | 3 | 13 | No. dependent on operational arrangements.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ-6 BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair / trolley hold
OFF-S9 OFF-1P-9 | Office - Single Person | Yes |  |  | 1 | 9 | 1 | 9 | 1 | 9 | NUM / Front of House coordinator. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | To be located in a non public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 5 6 bays (Acute + Fast Track) |  | 15 18 bays (Acute + Fast Track) |  | 30 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for waste water detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean / dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 8 | Ambulance service write up. 2 write up spaces within 5m2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 1 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 1 | 25 | 3 | 25 | 4 | 25 | Number of resus bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resucitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 16
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
CLUR-12 | Clean Utility / Medication Room | Yes | Shared |  | Shared |  | 1 | 12 | 1 | 14 | Includes small medication store with fridge and drug safe, to be shared between resuscitation bays.
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 4 | 1 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | For staff to meet with family and friends of patients. Also used as a quiet / grieving space. Number will depend on size of service. Also refer to allocation in acute zone below.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 5 6 bays (Adults + Paeds) |  | 10 12 Acute Bays (Adults + Paeds) |  | 14 18 Adult Acute Bays |  | 30 Adult Acute Bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 5 6 | 12 | 8 10 | 12 | 10 13 | 12 | 25 23 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N isolation | Yes |  |  |  |  | 1 | 15 | 1 2 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes |  |  |  |  | 1 | 15 (o) | 1 | 15 (o) | Positive pressure isolation.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 1 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  | 2 | 5 | 3 5 | 5 | 4 7 | 5 | Dedicated to each Class N, P, Class S room and O&G Room
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite - Standard | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room, Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes |  |  | 2 | 4 | 2 3 | 4 | 4 5 | 4
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 3 | 4
SHD | Shower - Accessible |  | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
CLUR-12 | Clean Utility / Medication Room | Yes | Shared |  | 1 | 10 | 1 | 12 | 2 | 12 | Include medication store where not provided separately.
MED-14 | Medication Room | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 4 | 1 | 4 | 2 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
STDR-10 | Medication Room | Yes | Shared |  |  |  | 1 | 10 | 1 | 10
BHWS-B | Bay - Handwashing,Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  | 1 | 1 (o) | 1 | 1 (o) | 2 | 1 (o) | 4 | 1(o) | Recessed wall mounted PPE holders may be provided between bedrooms instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 15 12 Paediatric Acute Bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 11 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 2 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [6 empty] | 1 | 15 (o) | Positive pressure isolation.
ANRM | Anteroom | Yes | [6 empty] | 1 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
CLUR-12 | Clean Utility / Medication Room | Yes |  |  |  |  | 1 | 8 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 4 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 4 | 1 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [5 empty] | 1 | 1 | 2 | 1 | Recessed wall mounted PPE holders may be provided between bedrooms instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 5 6 Fast Track Spaces |  | 10 12 Fast Track Spaces |  | 15 18 Fast Track Spaces
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 3 4 | 6.5 | 7 8 | 6.5 | 10 12 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 4 | 12 | 5 6 | 12 | The mix of bays and consult rooms will be dependent on project requirements.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16
| Consult - Dental | [5 empty] | 1 | 12 (o) | 1 | 12(o) | Determined by need/ activity. A knee break chair might be included to increase flexibility.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o)
| Store - Crutch | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE | [5 empty] | 2 | 1 | 3 | 1 | Recessed wall mounted PPE holders may be provided between bedrooms instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 5 6 bays (Acute + Fast Track) |  | 15 18 bays (Acute + Fast Track) |  | 30 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large foorprint.Weather protected to part of the area.
SUPPORT
AusHFG Room Code | Room / Space | SC / SC-D | 5 6 bays (Acute + Fast Track) |  | 15 18 bays (Acute + Fast Track) |  | 30 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track)
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN-9 STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster managament role.
DISP-8 DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service.
CLRM-5 CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 2 3 | 3 | For Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 6 bays |  | 12 bays |  | 20 bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 6 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite - Standard | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashin, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  | 1 | 1 | 2 | 1 | 3 | 1 | Recessed wall mounted PPE holders may be provided between bedrooms instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
CLUR-12 | Clean Utility / Medication Room | Yes |  |  | 1 | 10 (o) | 1 | 12 | 1 | 14
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM-5 CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV-OP BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT-4 BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 5 6 bays |  | 15 18 bays |  | 30 36 bays |  | 60 bays
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2 | Remarks
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30
CHST-20 CHST-10 CHST-35 | Change - Staff (Male/Female) | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
PROP-2 BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-S12 OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-S9 OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
STPS-8 | Store - Photocopy / Stationery | Yes | Shared |  | 1 | 8 4 | 1 | 8 4 | 1 | 8 4
MEET-L-20 MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-12 MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V1 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2 (o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  |  |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. To be shared between waiting area and clinical zone if provided.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE -1/2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. Final design & visual / acoustic separation will be dependent on MoC. Optional enclosed multifunction assessment room may be provided for patients who present with acute mental health issues, violence & assault, neurodiversity, depending on MoC.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair / trolley hold
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM / Front of House coordinator / local cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for waste water detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean / dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 8 10 | Ambulance service write up. 2 write up spaces within 5m2.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resus bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resucitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 16
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
CLUR-12 | Clean Utility / Medication Room | Yes | Shared |  | Shared |  | 1 | 12 | 1 | 14 | Includes small medication store with fridge and drug safe, to be shared between resuscitation bays.
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 4 | 1 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | For staff to meet with family and friends of patients. Also used as a quiet / grieving space. Number will depend on size of service. Also refer to allocation in acute zone below.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 5 6 | 12 | 8 10 | 12 | 10 13 | 12 | 25 23 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N isolation | Yes |  |  |  |  | 1 | 15 | 1 2 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes |  |  |  |  | 1 | 15 | 1 | 15 | Positive pressure isolation.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14
| Ensuite | [5 empty] | 1 | 5 | 1 | 5 | Dedicated and adjacent to Obstetrics & Gynaecology Room.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 1 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  | 2 | 5 | 3 5 | 5 | 4 7 | 5 | Dedicated to each Class N, P, Class S room and O&G Room
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite - Standard | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes |  |  | 2 | 4 | 2 3 | 4 | 4 5 | 4
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 3 | 4
SHD | Shower - Accessible |  | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
CLUR-12 | Clean Utility / Medication Room | Yes | Shared |  | 1 | 10 | 1 | 12 | 2 | 12 | Include medication store where not provided separately.
MED-14 | Medication Room | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 4 | 1 | 4 | 2 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
STDR-10 | Medication Room | Yes | Shared |  |  |  | 1 | 10 | 1 | 10
BHWS-B | Bay - Handwashing,Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  | 1 | 1 (o) | 1 | 1 (o) | 2 | 1 (o) | 4 | 1(o) | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 11 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 2 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [6 empty] | 1 | 15 (o) | Optional. Positive pressure isolation.
ANRM | Anteroom | Yes | [6 empty] | 1 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
CLUR-12 | Clean Utility / Medication Room | Yes |  |  |  |  | 1 | 8 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 4 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 4 | 1 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [5 empty] | 1 | 1 | 2 | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 3 4 | 6.5 | 7 8 | 6.5 | 10 12 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 4 | 12 | 5 6 | 12 | The mix of bays and consult rooms will be dependent on project requirements.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16
| Consult - Dental | [5 empty] | 1 | 12 (o) | 1 | 12(o) | Determined by need/ activity. A knee break chair might be included to increase flexibility.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o)
| Store - Crutch | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  | 1 | 1 | 2 | 1 | 3 | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN-9 STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster managament role.
DISP-8 DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service.
CLRM-5 CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 2 3 | 3 | For Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite - Standard | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashin, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  | 1 | 1 | 2 | 1 | 3 | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
CLUR-12 | Clean Utility / Medication Room | Yes |  |  | 1 | 10 (o) | 1 | 12 | 1 | 14
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM-5 CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV-OP BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT-4 BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WCAC | Toilet - Accessible | Yes |  |  |  |  | Shared | 6 | 1 | 6 (o) | Unless readily available elsewhere.
WCPU | Toilet - Public | Yes | [6 empty] | 2 | 3 (o) | Allocation dependent on nearby amenities.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | [6 empty] | 1 | 3 (o)
| Library / Study Space | [5 empty] | 1 | 15 (o) | 1 | 30 (o) | Consider fixed and movable furniture for flexibility.
MEET-20 MEET-30 | Meeting / Lecture Room | Yes |  |  |  |  | 1 | 20 (o) | 1 | 30 (o) | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting / Seminar Room | Yes | [6 empty] | 1 | 15 (o) | Consider operable wall to provide as two smaller rooms for higher utilisation.
| Simulation Room | [7 empty] | 1 | 30 (o)
| Simulation Control Room | [7 empty] | 1 | 8 (o)
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30
CHST-20 CHST-10 CHST-35 | Change - Staff (Male/Female) | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
PROP-2 BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-S12 OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-S9 OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
STPS-8 BMFD-3 | Store - Photocopy / Stationery Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 8 3 | 1 | 8 3 | 1 | 8 3
MEET-L-20 MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-12 MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## Indicative ED Capacity Rev 8_V1 (hidden)
ED Zone | Indicative number of ED treatment spaces
Acute | 6 | 12 | 18 | 30
Paediatric | Included above | Included above | 6 | 12
Fast Track | Included above | 6 | 12 | 18
Total ED Capacity* | 6 | 18 | 36 | 60
Resuscitation Zone | 1 treatment/ resuscitation bay | 2 | 3 | 5
ED Short Stay Unit | No allocation | 8 | 12 | 20

## ED SOA Rev 8_V2 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2 (o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  |  |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. To be shared between waiting area and clinical zone if provided.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE -1/2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. Final design & visual / acoustic separation will be dependent on MoC. Optional enclosed multifunction assessment room may be provided for patients who present with acute mental health issues, violence & assault, neurodiversity, depending on MoC.
| Triage Assessment Desk |  |  |  |  | 6.5(o) |  | 6.5(o) |  | 6.5(o) | May be provided instead or in combination with Triage Assessment Room depending on triage model. | TBC Total combined area for allocation of triage desks and assessment rooms.
| Bay - Fridge |  |  |  | Shared | 1 | 1 | 1 | 1 | 1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. | Comment from ERG 2 SC Meeting
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair / trolley hold
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM / Front of House coordinator / local cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for waste water detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean / dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 8 10 | Ambulance service write up. 2 write up spaces within 5m2.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resus bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resucitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 16
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
CLUR-12 | Clean Utility / Medication Room | Yes | Shared |  | Shared |  | 1 | 12 | 1 | 14 | Includes small medication store with fridge and drug safe, to be shared between resuscitation bays.
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | For staff to meet with family and friends of patients. Also used as a quiet / grieving space. Number will depend on size of service. Also refer to allocation in acute zone below.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 5 6 | 12 | 8 10 | 12 | 10 13 | 12 | 25 23 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N isolation | Yes |  |  |  |  | 1 | 15 | 1 2 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [5 empty] | 15(o) | 1 | 15(o) | Positive pressure isolation. Provision dependent on service provision e.g trauma burns.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14 | May be used for sexual assault examination in non-designated site.
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 | 1 | 5 | Dedicated and adjacent to Obstetrics & Gynaecology Room.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 1 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  | 2 | 5 | 3 5 | 5 | 4 7 | 5 | Dedicated to each Class N, P, Class S room and O&G Room
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite - Standard | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes |  |  | 2 | 4 | 2 3 | 4 | 4 5 | 4
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 3 | 4
SHD | Shower - Accessible |  | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
CLUR-12 | Clean Utility / Medication Room | Yes | Shared |  | 1 | 10 | 1 | 12 | 2 | 12 | Include medication store where not provided separately.
MED-14 | Medication Room | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 4 | 1 | 4 | 2 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
STDR-10 | Medication Room | Yes | Shared |  |  |  | 1 | 10 | 1 | 10
BHWS-B | Bay - Handwashing,Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  | 1 | 1 (o) | 1 | 1 (o) | 2 | 1 (o) | 4 | 1(o) | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 11 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 2 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [6 empty] | 1 | 15 (o) | Optional. Positive pressure isolation.
ANRM | Anteroom | Yes | [6 empty] | 1 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
CLUR-12 | Clean Utility / Medication Room | Yes |  |  |  |  | 1 | 8 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 4 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 4 | 1 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [5 empty] | 1 | 1 | 2 | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV-OP BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 3 4 | 6.5 | 7 8 | 6.5 | 10 12 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 4 | 12 | 5 6 | 12 | The mix of bays and consult rooms will be dependent on project requirements.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16
| Consult - Dental | [5 empty] | 1 | 12 (o) | 1 | 12(o) | Determined by need/ activity. A knee break chair might be included to increase flexibility.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o)
| Store - Crutch | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  | 1 | 1 | 2 | 1 | 3 | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ-4 BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN-9 STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster managament role.
DISP-8 DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service.
CLRM-5 CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 2 3 | 3 | For Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite - Standard | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashin, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  | 1 | 1 | 2 | 1 | 3 | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
CLUR-12 | Clean Utility / Medication Room | Yes |  |  | 1 | 10 (o) | 1 | 12 | 1 | 14
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM-5 CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV-OP BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT-4 BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 30 (o)
| Simulation Control Room | [7 empty] | 1 | 8 (o)
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30
CHST-20 CHST-10 CHST-35 | Change - Staff (Male/Female) | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
PROP-2 BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-S12 OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-S9 OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
STPS-8 BMFD-3 | Store - Photocopy / Stationery Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 8 3 | 1 | 8 3 | 1 | 8 3
MEET-L-20 MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-12 MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V3 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 6(o) | 1 | 6 | 1 | 6 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2(o) | 1 | 2(o) | 1 | 2(o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2(o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6(o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  |  |  | 1 | 12(o) | 1 | 12(o) | 1 | 12(o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE -1/2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of / or in combination with Triage Desks depending on triage model. | Final design & visual / acoustic separation will be dependent on MoC.
| Triage Assessment Desk |  |  |  |  | 6.5(o) |  | 6.5(o) |  | 6.5(o) | May be provided instead of / or in combination with Triage Rooms depending on triage model. | Area allocation allows up to 2 x Triage Desk for each Triage Room replacement.
| Bay - Fridge |  |  |  | Shared | 1 | 1 | 1 | 1 | 1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. | Comment from ERG 2 SC Meeting
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair / trolley hold
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM / Front of House coordinator / local cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for waste water detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean / dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. 2 write up spaces within 5m2. | Comment from Amb FG meeting
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resus bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 16
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | For staff to meet with family and friends of patients. Also used as a quiet / grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 13 | 12 | 23 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N isolation | Yes |  |  |  |  | 1 | 15 | 3 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [5 empty] | 15(o) |  | 15(o) | Optional. Positive pressure isolation. Provision dependent on service provision.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14 | May be used for sexual assault examination in non-designated site. | Mandated in ED as per ERG Meeting
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 | 1 | 5 | Dedicated and adjacent to Obstetrics & Gynaecology Room. | Mandated in ED as per ERG Meeting
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 3 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  | 2 | 5 | 3 | 5 | 6 | 5 | Dedicated to each Class N, P and Class S room.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite - Standard | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes |  |  | 2 | 4 | 2 | 4 | 4 | 4
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 3 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma. | Qty TBC
SHD | Shower - Accessible |  | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 6 | 2 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
STDR-10 | Medication Room | Yes | Shared |  |  |  | 1 | 10 | 1 | 10 |  | TBC
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10(o) | 1 | 15(o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5(o) | 1 | 10(o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g trauma burns.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 |  | Qty TBC
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 11 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. | No of Consult retained as per ERG comment
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16(o) | 1 | 16
| Consult - Dental | [5 empty] | 1 | 12(o) | 1 | 12(o) | Determined by need/ activity. A knee break chair might be included to increase flexibility. | TBC with ERG
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14(o) | 1 | 14(o)
| Store - Crutch | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20(o) | 1 | 40(o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12(o) | 1 | 12(o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster managament role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 2 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite - Standard | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25(o)
| Simulation Control Room | [7 empty] | 1 | 8(o)
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30
CHST-10 CHST-35 | Change - Staff (Male/Female) | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9(o) | 1 | 9(o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V4 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 6(o) | 1 | 6 | 1 | 6 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2(o) | 1 | 2(o) | 1 | 2(o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2(o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6(o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  |  |  | 1 | 12(o) | 1 | 12(o) | 1 | 12(o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE -1/2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of / or in combination with Triage Desks depending on triage model. | Final design & visual / acoustic separation will be dependent on MoC.
| Triage Assessment Desk |  |  |  |  | 6.5(o) |  | 6.5(o) |  | 6.5(o) | May be provided instead of / or in combination with Triage Rooms depending on triage model. | Area allocation allows up to 2 x Triage Desk for each Triage Room replacement.
| Bay - Fridge |  |  |  | Shared | 1 | 1 | 1 | 1 | 1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. | Comment from ERG 2 SC Meeting
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair / trolley hold
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM / Front of House coordinator / local cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for waste water detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean / dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. 2 write up spaces within 5m2. | Comment from Amb FG meeting
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resus bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 16
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | For staff to meet with family and friends of patients. Also used as a quiet / grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 13 | 12 | 23 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N isolation | Yes |  |  |  |  | 1 | 15 | 3 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [5 empty] | 15(o) |  | 15(o) | Optional. Positive pressure isolation. Provision dependent on service provision.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14 | May be used for sexual assault examination in non-designated site. | Mandated in ED as per ERG Meeting
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 | 1 | 5 | Dedicated and adjacent to Obstetrics & Gynaecology Room. | Mandated in ED as per ERG Meeting
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 3 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  | 2 | 5 | 3 | 5 | 6 | 5 | Dedicated to each Class N, P and Class S room.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite - Standard | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes |  |  | 2 | 4 | 2 | 4 | 4 | 4
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 3 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma. | Qty TBC
SHD | Shower - Accessible |  | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 6 | 2 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
STDR-10 | Medication Room | Yes | Shared |  |  |  | 1 | 10 | 1 | 10 |  | TBC
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10(o) | 1 | 15(o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5(o) | 1 | 10(o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g trauma burns.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 |  | Qty TBC
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 11 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. | No of Consult retained as per ERG comment
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16(o) | 1 | 16
| Consult - Dental | [5 empty] | 1 | 12(o) | 1 | 12(o) | Determined by need/ activity. A knee break chair might be included to increase flexibility. | TBC with ERG | To be deleted but added to HPU to be provided in ED with specialised services.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14(o) | 1 | 14(o)
| Store - Crutch | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20(o) | 1 | 40(o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12(o) | 1 | 12(o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster managament role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 2 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite - Standard | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay / wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25(o)
| Simulation Control Room | [7 empty] | 1 | 8(o)
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30
CHST-10 CHST-35 | Change - Staff (Male/Female) | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9(o) | 1 | 9(o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V5 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2 (o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  |  |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE -1/2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model. | Final design & visual / acoustic separation will be dependent on MoC.
| Triage Assessment Desk |  |  |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | May be provided instead of/or in combination with Triage Rooms depending on triage model. | Area allocation allows up to 2 x Triage Desk for each Triage Room replacement.
| Bay - Fridge |  |  |  | Shared | 1 | 1 | 1 | 1 | 1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. | Comment from ERG 2 SC Meeting
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/trolley hold
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for waste water detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. 2 write up spaces within 5m2. | Comment from Amb FG meeting
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resus bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 16 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 13 | 12 | 23 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N isolation | Yes |  |  |  |  | 1 | 15 | 3 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14 | May be used for sexual assault examination in non-designated site. | Mandated in ED as per ERG Meeting
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 | 1 | 5 | Dedicated and adjacent to Obstetrics & Gynaecology Room. | Mandated in ED as per ERG Meeting
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 3 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  | 2 | 5 | 3 | 5 | 6 | 5 | Dedicated to each Class N, P and Class S room.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite - Standard | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes |  |  | 2 | 4 | 2 | 4 | 3 | 4
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 2 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 3 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma. | Qty TBC
SHD | Shower - Accessible |  | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 6 | 2 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
STDR-10 | Medication Room | Yes | Shared |  |  |  | 1 | 10 | 1 | 10 |  | TBC
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g trauma burns.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 1 | 4
WCAC | Toilet - Accessible | Yes | [6 empty] | 1 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 1 | 4 |  | Qty TBC
| Shower - Accessible | [7 empty] | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 11 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. | No of Consult retained as per ERG comment
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o)
| Store - Crutch Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster managament role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 2 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite - Standard | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o)
| Simulation Control Room | [7 empty] | 1 | 8 (o)
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30
CHST-10 CHST-35 | Change - Staff (Male/Female) | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V6 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  |  |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE -1/2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model. | Final design & visual / acoustic separation will be dependent on MoC.
| Triage Assessment Desk |  |  |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | May be provided instead of/or in combination with Triage Rooms depending on triage model. | Area allocation allows up to 2 x Triage Desk for each Triage Room replacement.
| Bay - Fridge |  |  |  | Shared | 1 | 1 | 1 | 1 | 1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. | Comment from ERG 2 SC Meeting
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/trolley hold & linen
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for waste water detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. 2 write up spaces within 5m2. | Comment from Amb FG meeting
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resus bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 16 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 13 | 12 | 23 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N isolation | Yes |  |  |  |  | 1 | 15 | 3 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14 | May be used for sexual assault examination in non-designated site. | Mandated in ED as per ERG Meeting
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 | 1 | 5 | Dedicated and adjacent to Obstetrics & Gynaecology Room. | Mandated in ED as per ERG Meeting
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 3 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  | 2 | 5 | 3 | 5 | 6 | 5 | Dedicated to each Class N, P and Class S room.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite - Standard | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes |  |  | 1 2 | 4 | 2 | 4 | 3 | 4
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 2 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 3 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma. | Qty TBC
SHD | Shower - Accessible |  | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 6 | 2 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
STDR-10 | Medication Room | Yes | Shared |  |  |  | 1 | 10 | 1 | 10 |  | TBC
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g trauma burns.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 1 | 4
WCAC | Toilet - Accessible | Yes | [6 empty] | 1 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 1 | 4 |  | Qty TBC
| Shower - Accessible | [7 empty] | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 11 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. | No of Consult retained as per ERG comment
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12 spaces scenario
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional
| Store - Crutch Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster managament role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 2 3 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite - Standard | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IP&C policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8 | Optional for 8 bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff (Male/Female) | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## HPU 300_8 SOA
HPU 300 Emergency Unit - Schedule of Accommodation, Revision 8
ENTRY / PUBLIC AMENITIES
Room Code | Room Name | SC/ SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock - Entry | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 3 | 3 | Allocation dependent on nearby amenities. Toilet numbers provided are indicative only and must comply with the recommendations of building surveyors in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Accessible Changing Facility |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Toilet facilities for people with high support needs may be provided if not provided elsewhere (refer to 'Changing Places' information for Australian facilities). Larger area will be required if shower is to be provided. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for min 2 staff, 20m2 for min 3 staff & 30m2 for min 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 (o) | 1 | 1 (o) | Optional. Separate fridge (with optional freezer) for medications and drinks e.g. hydration fluids shared by all Triage spaces to support waiting room medicine. Provide if local jurisdictional policies for medication storage allows its provision.
BHW | Bay - Height / Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 1 | 7 | 1 | 10 | Wheelchair/trolley hold.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non-public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry.
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. Final spaces dependent on write-up spaces required and peak number of ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | Shared |  | 1 | 4
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
Room Code | Room Name | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 5 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning. Consider visual and acoustic privacy for children if paediatric resuscitation bay is collocated. May be enclosed if there is a requirement for humidity control and containment.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [7 empty] | 30 (o) | Optional. Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTV | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
Room Code | Room Name | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 | Dedicated to each Class N Room.
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 2 | 5 | 3 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Adjacent to allocated bariatric bay.
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Optional. Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Optional. Attached to the Consult Room - Sexual Assault
PROC | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Optional. Included under paediatric zone below for smaller services.
INTV | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 | Optional for 6-bay scenario depending on location of nearby patient amenities. Final number in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-10 SSTN-14 SSTN-20 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30 | 60-bed scenario may provide 2 x 15m2 Staff Stations instead.
| Staff Station, Emergency Control | [6 empty] | 14 (o) TBC | 1 | 14 (o) TBC | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 14 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. May be a combined room in 60-bed scenario.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design.
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube Station | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1 | Consider additional BPTS in Resuscitation Area if location cannot be centralised.
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and Ambulatory Care zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and Ambulatory Care zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
PAEDIATRIC ZONE
Room Code | Room Name | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-S | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone is provided.
PLAY | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 (o) | 1 | 6 (o) | Optional, where separate paediatric zone is provided. Provide baby change table.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room.
ENS-ST-C | Ensuite | Yes |  |  |  |  | 2 | 5 | 4 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
PROC | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTV | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 2 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S DTUR-10 | Dirty Utility | Yes |  |  |  |  | 1 | 8 | 1 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
TREATMENT AREAS - AMBULATORY CARE
Room Code | Room Name | SC / SC-D |  |  | 6 Ambulatory Care Spaces |  | 12 Ambulatory Care Spaces |  | 18 Ambulatory Care Spaces |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-S | Waiting - Sub | Yes |  |  |  |  | 1 | 10 | 1 | 15 | May require a public toilet if not provided nearby.
PBTR-FT | Patient Bay, Emergency - Ambulatory Care | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. One room to be attached or adjacent to a WC for Obstetrics/ Gynaecology patients.
CONS-ENT-OP | Consult - ENT / Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12-space scenario.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional. Consider locating plaster sink in Procedure Room instead if appropriate.
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 3 | 1 | 4 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 | Access to shower may also be required for areas where water immersion treatment is commonly used e.g. for jellyfish stings.
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 40-45%
OUTDOOR AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility. May be located in main ED or in the Staff Zone.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role. Consider convenient location for ambulance area.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement and qty will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit. Consider convenient location for ambulance area if dedicated ambulance Cleaner's Room is not provided.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 4 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
ED SHORT STAY UNIT
Room Code | Room Name | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation. May also be used for patients requiring palliative care.
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 4 | 5 | Provide for Class S room depending on service profile. Remainder shared between other bays/rooms.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S DTUR-10 | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 10 | Optional for 8-bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Consider adjacency to palliative care bedroom if provided in this zone.
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy.
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional.
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional.
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V8 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 | 1 | 1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/trolley hold & linen
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non-public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. 2 write up spaces within 5m2. Final spaces dependent on peak number of ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Inclusion dependent on service provision.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14 | May be used for sexual assault examination in non-designated site. May also be located in Fast Track depending on models of care.
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 | 1 | 5 | Attached or adjacent to Obstetrics & Gynaecology Room.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite | Yes |  |  | 2 | 5 | 3 | 5 | 5 | 5 | Dedicated to each Class N, P and Class S room.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 | Optional for 6 bay scenario depending on location of nearby patient amenities.
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 2 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
| Staff Station, Emergency Control | [6 empty] | 14 (o) TBC | 1 | 14 (o) TBC | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 12 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g trauma burns.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12 spaces scenario
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 3 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8 | Optional for 8 bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V7 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities. Changing Places toilet amenities should also be provided in this area if not provided elsewhere in the facility.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  |  |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 | 1 | 1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/trolley hold & linen
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non-public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. 2 write up spaces within 5m2. Final spaces dependent on peak number of ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 23 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 3 | 15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Inclusion dependent on service provision.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 | 1 | 14 | May be used for sexual assault examination in non-designated site.
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 | 1 | 5 | Dedicated and adjacent to Obstetrics & Gynaecology Room.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 3 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite | Yes |  |  | 2 | 5 | 3 | 5 | 6 | 5 | Dedicated to each Class N, P and Class S room.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 | Optional for 6 bay scenario depending on location of nearby patient amenities.
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 2 | 6
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
| Staff Station, Emergency Control | [6 empty] | 14 (o) TBC | 1 | 14 (o) TBC | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 12 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g trauma burns.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12 spaces scenario
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 3 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8 | Optional for 8 bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Comparison_V2 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access. Increase in line with previously endorsed Standard Component therefore excluded from analysis.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas. Increase in line with previously endorsed Standard Component therefore excluded from analysis.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional. Optional inclusion in line with benchmarking with recently delivered facilities. Excluded from analysis as inclusion is on project-by-project basis.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2 | Decrease in line with previously endorsed Standard Component therefore excluded from analysis.
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED. Added in line with DDA compliance. Excluded from analysis as provision is dependent on location of ED in relation to main hospital facilities.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | 0
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 +26 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model. Increase in 18 & 36 bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis. Increase in 60 bay scenario in line with ERG recommendation to improve forward movement of patients from waiting room into ED based on their experience with overcrowding in the waiting areas.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model. Optional inclusion in line with ERG recommendation and benchmarking with some recently delivered facilities. Excluded from analysis as provision is dependent on models of care and operational model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 +1 | 1 | 1 +1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. Room added in line with benchmarking with recently built facilities.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/trolley hold & linen
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non- public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  |  |  | 0 |  | +1 |  | +27
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 +2 | Ambulance service write up. 2 write up spaces within 5m2. Final spaces dependent on peak number of ambulance officers. Increase in line with recommendation from Ambulance Focus Group to provide adequate space for ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  | 0 |  | 0 |  | 0 |  | +2
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning. Increase in 2 Resus Bay scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 +9 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis. Increase in line with ACEM, ECI and ERG recommendation to provide a more functional resuscitation space in smaller ED as the room require the same number of staff during resus. The room is also often used as ICU space if patient transfer to a larger facility is delayed.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  | +9 |  | 0 |  | 0 |  | 0
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 -12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided. Increase for 6, 12 & 18 Bays scenarios in line with change of scenario bed space numbers therefore excluded from the analysis. Decrease for 30 Bays scenarios in line with ERG recommendation of providing more negative pressure bed rooms. Final qty provision dependent on models of care therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 +15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic. Increase for 30 Bays scenarios in line with ERG recommendation of providing more negative pressure bed rooms to better manage patients with airborne infections. Benchmarking also showed higher number of negative rooms in larger EDs.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Inclusion dependent on service provision. Provision is recommended only in specialised ED and dependent on models of care and ED services provision therefore excluded from the analysis.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 +14 | 1 | 14 +14 | May be used for sexual assault examination in non-designated site. May also be located in Fast Track depending on models of care. Increase in line with ERG recommendation that this room provision is recommended in new EDs.
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 +5 | 1 | 5 +5 | Attached or adjacent to Obstetrics & Gynaecology Room. Increase in line with ERG recommendation that ensuite provision is provided dedicated to Obstetrics & Gynaecology Room.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 +6 | Dedicated to each Class N Room Increase for 30 Bays scenarios in line with provision of more negative pressure bed rooms.
ENS-ST-C | Ensuite | Yes |  |  | 2 | 5 | 3 | 5 | 5 | 5 +5 | Dedicated to each Class N, P and Class S room. Increase for 30 Bays scenarios in line with provision of more negative pressure bed rooms.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 -4 | Optional for 6 bay scenario depending on location of nearby patient amenities. Increase for 6 bay scenario to show optional WC where no other WC is provided nearby therefore not included in analysis. Decrease for 60 bays scenario in line with ERG recommendation to improve accessibility for large number of patients (swapped for accessible WC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 2 | 6 +6 | Increase for 60 bays scenario in line with ERG recommendation to improve accessibility for large number of patients.
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 -8 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma. Decrease in line with ERG recommendation (as Showers not used often) and benchmarking with recently delivered facilities.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
| Staff Station, Emergency Control | [5 empty] | 1 | 14 (o) | 1 | 14 (o) | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc. Optional inclusion in line with ERG recommendation and benchmarking with some recently delivered facilities. Excluded from analysis as provision is dependent on models of care and ED local/regional responsibilities.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 12 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  | 0 |  | 0 |  | +19 |  | +27
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12 | Decrease for 12 Bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g. trauma burns. Optional inclusion in line with ERG recommendation. Excluded from analysis as provision is dependent on models of care and ED service provision.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4 -4 | Decrease in line with ERG recommendation to improve accessibility for large number of patients (swapped for accessible WC).
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 +6 | Increase for 12 bays scenario in line with ERG recommendation to improve accessibility for large number of patients.
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Decrease in line with ERG recommendation to improve accessibility for patients (swapped for accessible shower which is same size) therefore change not included in analysis.
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4 | Increase in line with ERG recommendation to improve accessibility for patients(swapped for standard shower which is same size) therefore change not included in analysis.
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation | [6 empty] | 0 |  | +2
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements. Increase in line with change of scenario bed space numbers therefore excluded from the analysis.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 -12 | The mix of bays and consult rooms will be dependent on project requirements. Decrease in line with ERG recommendation and benchmarking with recently delivered facilities.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12 spaces scenario
| Consult - Dental | [6 empty] | 12(o) -12 |  | 12(o) -12 | Determined by need/activity. A knee break chair might be included to increase flexibility. Deletion of room in line with ERG recommendation and benchmarking with recently delivered facilities.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  |  |  | 0 |  | -12 |  | -24
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area. Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as although they are highly desirable, it is not always possible to provide in projects.
| Sub-Total Variation | [6 empty] | 0 |  | 0
SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 3 | 3 +3 | Distributed in close proximity from clinical areas. Increase in line with ERG recommendation for better distributed locations within a larger clinical zone and potential multiple pods but final qty dependent on overall staff numbers and ED layout.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | +3
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements. Increase for 8 Bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8 | Optional for 8 bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | 0
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as inclusion is dependent on operational policies.
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as inclusion is dependent on operational policies.
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
| Sub-Total Variation | [8 empty] | 0
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation. Excluded from analysis as provision is dependent on location of ED in relation to hospital staff facilities.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 -5 | 1 | 3 -5 | 1 | 3 -5 | Decrease in line with the change in work practices to reduce paper requirements.
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
| Sub-Total Variation |  |  | 0 |  | -5 |  | -5 |  | -5
| Total Variation |  |  | 9 |  | -5 |  | +3 |  | +32

## ED SOA Comparison_V1 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access. Increase in line with previously endorsed Standard Component therefore excluded from analysis.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas. Increase in line with previously endorsed Standard Component therefore excluded from analysis.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional. Optional inclusion in line with benchmarking with recently delivered facilities. Excluded from analysis as inclusion is on project-by-project basis.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2 | Decrease in line with previously endorsed Standard Component therefore excluded from analysis.
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  |  |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED. Added in line with DDA compliance. Excluded from analysis as provision is dependent on location of ED in relation to main hospital facilities.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | 0
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 +26 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model. Increase in 18 & 36 bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis. Increase in 60 bay scenario in line with ERG recommendation to improve forward movement of patients from waiting room into ED.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model. Optional inclusion in line with ERG recommendation and benchmarking with some recently delivered facilities. Excluded from analysis as provision is dependent on models of care and operational model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 +1 | 1 | 1 +1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. Room added in line with benchmarking with recently built facilities.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/trolley hold & linen
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non- public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  |  |  | 0 |  | +1 |  | +27
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 +2 | Ambulance service write up. 2 write up spaces within 5m2. Final spaces dependent on peak number of ambulance officers. Increase in line with recommendation from Ambulance Focus Group to provide adequate space for ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  | 0 |  | 0 |  | 0 |  | +2
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning. Increase in 2 Resus Bay scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 +9 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis. Increase in line with ACEM, ECI and ERG recommendation to provide a more functional resuscitation space in smaller ED as the room require the same number of staff during resus. The room is also often used as ICU space if patient transfer to a larger facility is delayed.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  | +9 |  | 0 |  | 0 |  | 0
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 23 | 12 -24 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided. Increase for 6, 12 & 18 Bays scenarios in line with change of scenario bed space numbers therefore excluded from the analysis. Decrease for 30 Bays scenarios in line with ERG recommendation of providing more negative pressure bed rooms. Final qty provision dependent on models of care therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 3 | 15 +30 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic. Increase for 30 Bays scenarios in line with ERG recommendation of providing more negative pressure bed rooms to better manage patients with airborne infections.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Inclusion dependent on service provision. Provision is recommended only in specialised ED and dependent on models of care and ED services provision therefore excluded from the analysis.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 +14 | 1 | 14 +14 | May be used for sexual assault examination in non-designated site. Increase in line with ERG recommendation that this room provision is recommended in new EDs.
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 +5 | 1 | 5 +5 | Dedicated and adjacent to Obstetrics & Gynaecology Room. Increase in line with ERG recommendation that ensuite provision is provided dedicated to Obstetrics & Gynaecology Room.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 3 | 6 +12 | Dedicated to each Class N Room Increase for 30 Bays scenarios in line with provision of more negative pressure bed rooms.
ENS-ST-C | Ensuite | Yes |  |  | 2 | 5 | 3 | 5 | 6 | 5 +10 | Dedicated to each Class N, P and Class S room. Increase for 30 Bays scenarios in line with provision of more negative pressure bed rooms.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 -4 | Optional for 6 bay scenario depending on location of nearby patient amenities. Increase for 6 bay scenario to show optional WC where no other WC is provided nearby therefore not included in analysis.. Decrease for 60 bays scenario in line with ERG recommendation to improve accessibility for large number of patients (swapped for accessible WC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 2 | 6 +6 | Increase for 60 bays scenario in line with ERG recommendation to improve accessibility for large number of patients.
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 -8 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma. Decrease in line with ERG recommendation (as Showers not used often) and benchmarking with recently delivered facilities.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
| Staff Station, Emergency Control | [5 empty] | 1 | 14 (o) | 1 | 14 (o) | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc. Optional inclusion in line with ERG recommendation and benchmarking with some recently delivered facilities. Excluded from analysis as provision is dependent on models of care and ED local/regional responsibilities.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 12 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  | 0 |  | 0 |  | +19 |  | +41
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12 | Decrease for 12 Bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g trauma burns. Optional inclusion in line with ERG recommendation. Excluded from analysis as provision is dependent on models of care and ED service provision.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4 -4 | Decrease in line with ERG recommendation to improve accessibility for large number of patients (swapped for accessible WC).
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 +6 | Increase for 12 bays scenario in line with with ERG recommendation to improve accessibility for large number of patients therefore change not included in analysis.
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Decrease in line with ERG recommendation to improve accessibility for patients (swapped for accessible shower which is same size) therefore change not included in analysis.
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4 | Increase in line with ERG recommendation to improve accessibility for patients(swapped for standard shower which is same size) therefore change not included in analysis.
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation | [6 empty] | 0 |  | +2
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements. Increase in line with change of scenario bed space numbers therefore excluded from the analysis.
CONS | Consult room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 -12 | The mix of bays and consult rooms will be dependent on project requirements. Decrease in line with ERG recommendation and benchmarking with recently delivered facilities.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12 spaces scenario
| Consult - Dental | [6 empty] | 12(o) -12 |  | 12(o) -12 | Determined by need/ activity. A knee break chair might be included to increase flexibility. Deletion of room in line with ERG recommendation and benchmarking with recently delivered facilities.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  |  |  | 0 |  | -12 |  | -24
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area. Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as although they are highly desirable, it is not always possible to provide in projects.
| Sub-Total Variation | [6 empty] | 0 |  | 0
SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 3 | 3 +3 | Distributed in close proximity from clinical areas. Increase in line with ERG recommendation for better distributed locations within clinical zones but final qty dependent on overall staff WC provision therefore excluded from analysis.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | +3
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements. Increase for 8 Bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8 | Optional for 8 bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | 0
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as inclusion is dependent on operational policies.
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as inclusion is dependent on operational policies.
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
| Sub-Total Variation | [8 empty] | 0
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation. Excluded from analysis as provision is dependent on location of ED in relation to hospital staff facilities.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 -5 | 1 | 3 -5 | 1 | 3 -5 | Decrease in line with the change in work practices to reduce paper requirements.
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
| Sub-Total Variation |  |  | 0 |  | -5 |  | -5 |  | -5
| Total Variation |  |  | 9 |  | -5 |  | +3 |  | +46

## ED SOA Rev 8_V9 (hidden)
HPU 300 Emergency Unit - Schedule of Accommodation, Revision 8
ENTRY / PUBLIC AMENITIES
Room Code | Room Name | SC/ SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 3 | 3 | Allocation dependent on nearby amenities. Toilet numbers provided are indicative only and must comply with the recommendations of building surveyors in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Changing Places toilet amenities should be provided if not provided elsewhere in the facility. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for min 2 staff, 20m2 for min 3 staff & 30m2 for min 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 (o) | 1 | 1(o) | Separate fridge for medications and drinks e.g. hydration fluids shared by all Triage spaces to support waiting room medicine. Provide if local jurisdictional policies for medication storage allows its provision.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 1 | 7 | 1 | 10 | Wheelchair/trolley hold
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non-public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. Final spaces dependent on write-up spaces required and peak number of ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | Shared |  | 1 | 4
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
Room Code | Room Name | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 5 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [7 empty] | 30 (o) | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
Room Code | Room Name | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Inclusion dependent on service provision.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 2 | 5 | 3 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Adjacent to allocated bariatric bay
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 | Optional for 6 bay scenario depending on location of nearby patient amenities. Final number in accordance with the National Construction Code (NCC)
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-10 SSTN-14 SSTN-20 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30 | 60 bed scenario may provide 2 x 15m2 Staff Stations instead.
| Staff Station, Emergency Control | [6 empty] | 14 (o) TBC | 1 | 14 (o) TBC | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 14 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. May be a combined room in 60 bed scanario.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
PAEDIATRIC ZONE
Room Code | Room Name | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6 | Optional, where separate paediatric zone provided. Provide baby change table.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g trauma burns.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite | Yes |  |  |  |  | 2 | 5 | 4 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6
SHPT | Shower - Patient | Yes
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 2 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S DTUR-10 | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 10 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
TREATMENT AREAS - FAST TRACK
Room Code | Room Name | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15 | May require a public toilet if not provided nearby.
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. One room to be attached or adjacent to a WC for Obstetrics/ Gynaecology patients.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12 spaces scenario
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 3 | 1 | 4 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 40-45%
OUTDOOR AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility. May be located in main ED or in the Staff Zone.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role. Consider convenient location for ambulance area.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement and qty will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit. Consider convenient location for ambulance area.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 4 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
SHORT STAY UNIT
Room Code | Room Name | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 4 | 5 | Provide for Class S room depending on service profile. Remainder shared between other bays/rooms.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S DTUR-10 | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 10 | Optional for 8 bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V11 (hidden)
HPU 300 Emergency Unit - Schedule of Accommodation, Revision 8
ENTRY / PUBLIC AMENITIES
Room Code | Room Name | SC/ SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments | Comment
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock - Entry, 12m2 | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access. | The name is Airlock - Entry, 12m2.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 3 | 3 | Allocation dependent on nearby amenities. Toilet numbers provided are indicative only and must comply with the recommendations of building surveyors in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Accessible Changing Facility |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Toilet facilities for people with high support needs may be provided if not provided elsewhere (refer to 'Changing Places' information for Australian facilities). Larger area will be required if shower is to be provided. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for min 2 staff, 20m2 for min 3 staff & 30m2 for min 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 (o) | 1 | 1 (o) | Optional. Separate fridge (with optional freezer) for medications and drinks e.g. hydration fluids shared by all Triage spaces to support waiting room medicine. Provide if local jurisdictional policies for medication storage allows its provision. | Should the word Optional be noted?
BHW | Bay - Height/Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2 |  | The name is Bay - Height/Weight
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 1 | 7 | 1 | 10 | Wheelchair/trolley hold. | Full stop is missing after hold.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non-public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry. | Full stop after entry.
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. Final spaces dependent on write-up spaces required and peak number of ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | Shared |  | 1 | 4
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
Room Code | Room Name | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 5 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning. Consider visual and acoustic privacy for children if paediatric resuscitation bay is collocated. May be enclosed if there is a requirement for humidity control and containment.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [7 empty] | 30 (o) | Optional. Larger sized resuscitation bay for designated trauma services. | PBTR-R is not the code for this one, as PBTR-R does not have the word 'Trauma' in the name. The word Optional is missing. | The room will still be the same, just larger. And 'Trauma' needs to be in the name.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTV | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone. | The code is INTV
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
Room Code | Room Name | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 | Dedicated to each Class N Room. | Full stop in missing
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 2 | 5 | 3 | 5 | For all Class N rooms. Provide for Class S room depending on service profile. | The name is Ensuite - Back to Back | Although named 'back-to-back' in SC these rooms are not in ED. They are stand-alone but looks exactly like a single back-to-back ensuite.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Adjacent to allocated bariatric bay. | Full stop is missing
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Optional. Dedicated room required where ED is a designated sexual assault examination site. | The word Optional is missing
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Optional. Attached to the Consult Room - Sexual Assault | The word Optional is missing. The full stop is missing.
PROC | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Optional. Included under paediatric zone below for smaller services. | The code is PROC. The word Optional is missing
INTV | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above. | The code is INTV
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 | Optional for 6-bay scenario depending on location of nearby patient amenities. Final number in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-10 SSTN-14 SSTN-20 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30 | 60-bed scenario may provide 2 x 15m2 Staff Stations instead.
| Staff Station, Emergency Control | [6 empty] | 14 (o) TBC | 1 | 14 (o) TBC | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 14 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. May be a combined room in 60-bed scenario.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays. | Full stop is missing
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube Station | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1 | Consider additional BPTS in Resuscitation Area if location cannot be centralised. | The name is Bay - Pneumatic Tube Station
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and Ambulatory Care zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and Ambulatory Care zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
PAEDIATRIC ZONE
Room Code | Room Name | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-S | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone is provided. | The code is WAIT-S.
PLAY | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided. | The code is PLAY.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 (o) | 1 | 6 (o) | Optional, where separate paediatric zone is provided. Provide baby change table.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room. | Full stop is missing.
ENS-ST-C | Ensuite | Yes |  |  |  |  | 2 | 5 | 4 | 5 | For all Class N rooms. Provide for Class S room depending on service profile. | The name is Ensuite - Back to Back. | Although named 'back-to-back' in SC these rooms are not in ED. They are stand-alone but looks exactly like a single back-to-back ensuite.
PROC | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20 |  | The code is PROC.
INTV | Interview Room | [5 empty] | Share |  | 1 | 12 |  | The code is INTV.
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays. | Full stop is missing.
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 2 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S DTUR-10 | Dirty Utility | Yes |  |  |  |  | 1 | 8 | 1 | 10 | No. dependent on size and configuration of ED. | Full stop is missing.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
TREATMENT AREAS - AMBULATORY CARE
Room Code | Room Name | SC / SC-D |  |  | 6 Ambulatory Care Spaces |  | 12 Ambulatory Care Spaces |  | 18 Ambulatory Care Spaces |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-S | Waiting - Sub | Yes |  |  |  |  | 1 | 10 | 1 | 15 | May require a public toilet if not provided nearby. | The name is Waiting - Sub and the code is WAIT-S.
PBTR-FT | Patient Bay, Emergency - Ambulatory Care | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. One room to be attached or adjacent to a WC for Obstetrics/ Gynaecology patients.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12-space scenario. | Full stop is missing
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional. Consider locating plaster sink in Procedure Room instead if appropriate.
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 3 | 1 | 4 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 | Access to shower may also be required for areas where water immersion treatment is commonly used e.g. for jellyfish stings.
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 40-45%
OUTDOOR AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility. May be located in main ED or in the Staff Zone.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role. Consider convenient location for ambulance area.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement and qty will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit. Consider convenient location for ambulance area if dedicated ambulance Cleaner's Room is not provided.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 4 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
SHORT STAY UNIT
Room Code | Room Name | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation. May also be used for patients requiring palliative care.
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 4 | 5 | Provide for Class S room depending on service profile. Remainder shared between other bays/rooms. | The name is Ensuite - Back to Back. | Although named 'back-to-back' in SC these rooms are not in ED. They are stand-alone but looks exactly like a single back-to-back ensuite.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays. | Full stop is missing.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S DTUR-10 | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 10 | Optional for 8-bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Consider adjacency to palliative care bedroom if provided in this zone. | The name is Bay - Beverage
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy. | Full stop is missing.
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional. | Full stop is missing.
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional. | Full stop is missing.
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Rev 8_V10 (hidden)
HPU 300 Emergency Unit - Schedule of Accommodation, Revision 8
ENTRY / PUBLIC AMENITIES
Room Code | Room Name | SC/ SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 3 | 3 | Allocation dependent on nearby amenities. Toilet numbers provided are indicative only and must comply with the recommendations of building surveyors in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Changing Places toilet amenities should be provided if not provided elsewhere in the facility. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for min 2 staff, 20m2 for min 3 staff & 30m2 for min 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 (o) | 1 | 1(o) | Separate fridge for medications and drinks e.g. hydration fluids shared by all Triage spaces to support waiting room medicine. Provide if local jurisdictional policies for medication storage allows its provision.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 1 | 7 | 1 | 10 | Wheelchair/trolley hold
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non-public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. Final spaces dependent on write-up spaces required and peak number of ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | Shared |  | 1 | 4
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
Room Code | Room Name | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 5 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [7 empty] | 30 (o) | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
Room Code | Room Name | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 2 | 5 | 3 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Adjacent to allocated bariatric bay
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 | Optional for 6-bay scenario depending on location of nearby patient amenities. Final number in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-10 SSTN-14 SSTN-20 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30 | 60-bed scenario may provide 2 x 15m2 Staff Stations instead.
| Staff Station, Emergency Control | [6 empty] | 14 (o) TBC | 1 | 14 (o) TBC | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 14 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. May be a combined room in 60-bed scenario.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1 | Consider additional BPTS in Resuscitation Area if location cannot be centralised.
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
PAEDIATRIC ZONE
Room Code | Room Name | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 (o) | 1 | 6 (o) | Optional, where separate paediatric zone provided. Provide baby change table.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite | Yes |  |  |  |  | 2 | 5 | 4 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 2 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S DTUR-10 | Dirty Utility | Yes |  |  |  |  | 1 | 8 | 1 | 10 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
TREATMENT AREAS - FAST TRACK
Room Code | Room Name | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15 | May require a public toilet if not provided nearby.
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. One room to be attached or adjacent to a WC for Obstetrics/ Gynaecology patients.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12-space scenario
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional. Consider locating plaster sink in Procedure Room instead if appropriate.
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 3 | 1 | 4 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 | Access to shower may also be required for areas where water immersion treatment is commonly used e.g. jellyfish stings.
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 40-45%
OUTDOOR AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility. May be located in main ED or in the Staff Zone.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role. Consider convenient location for ambulance area.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement and qty will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit. Consider convenient location for ambulance area if dedicated ambulance Cleaner's Room is not provided.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 4 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
SHORT STAY UNIT
Room Code | Room Name | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation. May also be used for patients requiring palliative care.
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 4 | 5 | Provide for Class S room depending on service profile. Remainder shared between other bays/rooms.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S DTUR-10 | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 10 | Optional for 8-bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Consider adjacency to palliative care bedroom if provided in this zone.
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%

## ED SOA Comparison Summary V1 (hidden)
ED Functional Zone | Variation in Area Compared with ED HPU Revision 7 (m2)
Shared ED Areas - Indicative ED Capacities | 6 Spaces | 18 Spaces | 36 Spaces | 60 Spaces
Entry / Public Amenities - Area variation (m2) |  | +1 | +1 | -2
Triage / Registration - Area variation (m2) |  | 0 | +1 | +27
Ambulance Areas - Area variation (m2) | 0 | 0 | 0 | +2
Outdoor Areas - Area variation (m2) |  |  | 0 | 0
Support Areas - Area variation (m2) | 0 | 0 | 0 | +6
Education Areas (Optional) - Area variation (m2) |  |  |  | +35
Staff Areas - Area variation (m2) | 0 | -5 | -5 | -5
Resus Zone - assumed patient capacity | 1 Space | 2 Spaces | 3 Spaces | 5 Spaces
Area variation (m2) | +9 | 0 | 0 | -5
Acute Zone - assumed patient capacity | 6 Spaces | 12 Spaces | 18 Spaces | 30 Spaces
Area variation (m2) | 0 | -5 | -9 | -8
Paediatric Zone - assumed patient capacity | N/A | N/A | 6 Spaces | 12 Spaces
Area variation (m2) |  |  | +6 | +8
Fast Track - assumed patient capacity | N/A | 6 Spaces | 12 Spaces | 18 Spaces
Area variation (m2) | - | 0 | -12 | -24
Short Stay Unit - assumed patient capacity | N/A | 8 spaces | 12 spaces | 20 spaces
Area variation (m2) | 0 | 0 | 0 | -3
Total Change (m2) | +9 | -9 | -8 | +25

## ED SOA Rev 8_V12 COPY (hidden)
HPU 300 Emergency Unit - Schedule of Accommodation, Revision 8
ENTRY / PUBLIC AMENITIES
Room Code | Room Name | SC/ SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock - Entry | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 3 | 3 | Allocation dependent on nearby amenities. Toilet numbers provided are indicative only and must comply with the recommendations of building surveyors in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Accessible Changing Facility |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Toilet facilities for people with high support needs may be provided if not provided elsewhere (refer to 'Changing Places' information for Australian facilities). Larger area will be required if shower is to be provided. Location to allow shared use between waiting area and clinical zone if provided in ED.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TRIAGE / REGISTRATION
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for min 2 staff, 20m2 for min 3 staff & 30m2 for min 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 (o) | 1 | 1 (o) | Optional. Separate fridge (with optional freezer) for medications and drinks e.g. hydration fluids shared by all Triage spaces to support waiting room medicine. Provide if local jurisdictional policies for medication storage allows its provision.
BHW | Bay - Height / Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 1 | 7 | 1 | 10 | Wheelchair/trolley hold.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non-public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
AMBULANCE AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry.
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 | Ambulance service write up. Final spaces dependent on write-up spaces required and peak number of ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | Shared |  | 1 | 4
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
TREATMENT AREAS - RESUSCITATION
Room Code | Room Name | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 5 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning. Consider visual and acoustic privacy for children if paediatric resuscitation bay is collocated. May be enclosed if there is a requirement for humidity control and containment.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [7 empty] | 30 (o) | Optional. Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTV | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
TREATMENT AREAS - ACUTE
Room Code | Room Name | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 | Dedicated to each Class N Room.
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 2 | 5 | 3 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Adjacent to allocated bariatric bay.
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Optional. Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Optional. Attached to the Consult Room - Sexual Assault
PROC | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Optional. Included under paediatric zone below for smaller services.
INTV | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
Room Code | Room Name | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 | Optional for 6-bay scenario depending on location of nearby patient amenities. Final number in accordance with the National Construction Code (NCC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 1 | 6
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-10 SSTN-14 SSTN-20 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30 | 60-bed scenario may provide 2 x 15m2 Staff Stations instead.
| Staff Station, Emergency Control | [6 empty] | 14 (o) | 1 | 14 (o) | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 14 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. May be a combined room in 60-bed scenario.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design.
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube Station | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1 | Consider additional BPTS in Resuscitation Area if location cannot be centralised.
Room Code | Room Name | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and Ambulatory Care zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and Ambulatory Care zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
PAEDIATRIC ZONE
Room Code | Room Name | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-S | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone is provided.
PLAY | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 (o) | 1 | 6 (o) | Optional, where separate paediatric zone is provided. Provide baby change table.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room.
ENS-ST-C | Ensuite | Yes |  |  |  |  | 2 | 5 | 4 | 5 | For all Class N rooms. Provide for Class S room depending on service profile.
PROC | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTV | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 6
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4
Room Code | Room Name | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design.
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 2 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S DTUR-10 | Dirty Utility | Yes |  |  |  |  | 1 | 8 | 1 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
TREATMENT AREAS - AMBULATORY CARE
Room Code | Room Name | SC / SC-D |  |  | 6 Ambulatory Care Spaces |  | 12 Ambulatory Care Spaces |  | 18 Ambulatory Care Spaces |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-S | Waiting - Sub | Yes |  |  |  |  | 1 | 10 | 1 | 15 | May require a public toilet if not provided nearby.
PBTR-FT | Patient Bay, Emergency - Ambulatory Care | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 | The mix of bays and consult rooms will be dependent on project requirements. One room to be attached or adjacent to a WC for Obstetrics/ Gynaecology patients.
CONS-ENT-OP | Consult - ENT / Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12-space scenario.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
Room Code | Room Name | SC / SC-D |  |  | 6 Ambulatory Care Spaces |  | 12 Ambulatory Care Spaces |  | 18 Ambulatory Care Spaces |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional. Consider locating plaster sink in Procedure Room instead if appropriate.
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 3 | 1 | 4 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 | Access to shower may also be required for areas where water immersion treatment is commonly used e.g. for jellyfish stings.
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 40-45%
OUTDOOR AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area.
SUPPORT AREAS
Room Code | Room Name | SC / SC-D | 6 bays (Acute + Ambulatory Care) |  | 18 bays (Acute + Ambulatory Care) |  | 36 bays (Acute + Ambulatory Care) |  | 60 bays (Acute + Ambulatory Care) |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility. May be located in main ED or in the Staff Zone.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role. Consider convenient location for ambulance area.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement and qty will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit. Consider convenient location for ambulance area if dedicated ambulance Cleaner's Room is not provided.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 4 | 3 | Distributed in close proximity from clinical areas.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40-45%
ED SHORT STAY UNIT
Room Code | Room Name | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation. May also be used for patients requiring palliative care.
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 4 | 5 | Provide for Class S room depending on service profile. Remainder shared between other bays/rooms.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | Assigned at a rate of 1:4 to 1:6. Assume 1:4 during early planning and assess opportunities for more efficient allocation during schematic design.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 10 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies.
DTUR-S DTUR-10 | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 10 | Optional for 8-bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay - Beverage | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Consider adjacency to palliative care bedroom if provided in this zone.
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy.
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
EDUCATION AREAS (OPTIONAL)
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional.
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional.
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
STAFF AREAS
Room Code | Room Name | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Comments
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device | Yes | Shared |  | 1 | 3 | 1 | 3 | 1 | 3
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
[12 empty] | ED Zone | Indicative number of ED treatment spaces
[12 empty] | Acute | 6 | 12 | 18 | 30
[12 empty] | Paediatric | Included above | Included above | 6 | 12
[12 empty] | Ambulatory Care | Included above | 6 | 12 | 18
[12 empty] | Total ED Capacity* | 6 | 18 | 36 | 60
[12 empty] | Resuscitation Zone | 1 treatment/ resuscitation bay | 2 | 3 | 5
[12 empty] | ED Short Stay Unit | No allocation | 8 | 12 | 20

## ED Spatial Benchmarking (hidden)
|  | ADULT |  | PAEDS
| Triage | Total QTY of ED Acute Treatment Spaces | QTY of Neg Pressure | QTY of Bays | QTY of Neg Pressure | Resus Spaces
Blacktown | 2 rooms + 1 CIN | 24 | 1 | 4 | 1 | 5
Campbelltown | 4 rooms | 18 | 2 | 24 | 1 | 4A + 2P
Grafton Base Hospital |  | 23 | 1
Hornsby Ku-ring-gai Hospital Stage 2 | 1 room | 19 | 3 | 5 | 0 | 3
Liverpool | 3 rooms | 29 | 2 | 8 |  | 6
Nepean | 3 rooms | 36 | 1 | 8 | 0
Northern Beaches | 2 desks + 1 room | 20 | 1 | 8 | 2 | 3A + 1P
Royal North Shore Hospital |  | 30 | 1 | 12 | 1 | 5
Royal Prince Alfred Hospital | ? desks + 2 rooms | 76 | 4 | 12 | 1
Shellharbour Hospital | 2 rooms + 1 CIN | 19 | 1 |  | 1
St George |  | 34 | 1 | 11
Westmead | 6 rooms | 70 | 10 |  |  | 6 (1 iso)
Gold Coast Hospital | ? desks + 3 rooms | 32 | 2 | 8 | 1 | 4A+1P
Royal Adelaide | 4 rooms | 25 | 5 |  |  | 8

## ED SOA Comparison_V4 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access. Increase in line with previously endorsed Standard Component therefore excluded from analysis.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas. Increase in line with previously endorsed Standard Component therefore excluded from analysis.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional. Optional inclusion in line with benchmarking with recently delivered facilities. Excluded from analysis as inclusion is on project-by-project basis.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2 | Decrease in line with previously endorsed Standard Component therefore excluded from analysis.
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED. Added in line with DDA compliance. Excluded from analysis as provision is dependent on location of ED in relation to main hospital facilities.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | 0
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 +26 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model. Increase in 18 & 36 bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis. Increase in 60 bay scenario in line with ERG recommendation to improve forward movement of patients from waiting room into ED based on their experience with overcrowding in the waiting areas.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model. Optional inclusion in line with ERG recommendation and benchmarking with some recently delivered facilities. Excluded from analysis as provision is dependent on models of care and operational model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 +1 | 1 | 1 +1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. Room added in line with benchmarking with recently built facilities.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/trolley hold & linen
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non- public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  |  |  | 0 |  | +1 |  | +27
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 +2 | Ambulance service write up. 2 write up spaces within 5m2. Final spaces dependent on peak number of ambulance officers. Increase in line with recommendation from Ambulance Focus Group to provide adequate space for ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  | 0 |  | 0 |  | 0 |  | +2
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning. Increase in 2 Resus Bay scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 +9 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis. Increase in line with ACEM, ECI and ERG recommendation to provide a more functional resuscitation space in smaller ED as the room require the same number of staff during resus. The room is also often used as ICU space if patient transfer to a larger facility is delayed.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  | +9 |  | 0 |  | 0 |  | 0
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 -12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided. Increase for 6, 12 & 18 Bays scenarios in line with change of scenario bed space numbers therefore excluded from the analysis. Decrease for 30 Bays scenarios in line with ERG recommendation of providing more negative pressure bed rooms. Final qty provision dependent on models of care therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 +15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic. Increase for 30 Bays scenarios in line with ERG recommendation of providing more negative pressure bed rooms to better manage patients with airborne infections. Benchmarking also showed higher number of negative rooms in larger EDs.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Inclusion dependent on service provision. Provision is recommended only in specialised ED and dependent on models of care and ED services provision therefore excluded from the analysis.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 +6 | Dedicated to each Class N Room Increase for 30 Bays scenarios in line with provision of more negative pressure bed rooms.
ENS-ST-C | Ensuite | Yes |  |  | 2 | 5 | 3 | 5 | 5 | 5 +5 | Dedicated to each Class N, P and Class S room. Increase for 30 Bays scenarios in line with provision of more negative pressure bed rooms.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 -4 | Optional for 6 bay scenario depending on location of nearby patient amenities. Increase for 6 bay scenario to show optional WC where no other WC is provided nearby therefore not included in analysis. Decrease for 60 bays scenario in line with ERG recommendation to improve accessibility for large number of patients (swapped for accessible WC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 2 | 6 +6 | Increase for 60 bays scenario in line with ERG recommendation to improve accessibility for large number of patients.
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 -8 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma. Decrease in line with ERG recommendation (as Showers not used often) and benchmarking with recently delivered facilities.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
| Staff Station, Emergency Control | [5 empty] | 1 | 14 (o) | 1 | 14 (o) | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc. Optional inclusion in line with ERG recommendation and benchmarking with some recently delivered facilities. Excluded from analysis as provision is dependent on models of care and ED local/regional responsibilities.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 12 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  | 0 |  | 0 |  | 0 |  | +8
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12 | Decrease for 12 Bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g. trauma burns. Optional inclusion in line with ERG recommendation. Excluded from analysis as provision is dependent on models of care and ED service provision.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4 -4 | Decrease in line with ERG recommendation to improve accessibility for large number of patients (swapped for accessible WC).
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 +6 | Increase for 12 bays scenario in line with ERG recommendation to improve accessibility for large number of patients.
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Decrease in line with ERG recommendation to improve accessibility for patients (swapped for accessible shower which is same size) therefore change not included in analysis.
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4 | Increase in line with ERG recommendation to improve accessibility for patients(swapped for standard shower which is same size) therefore change not included in analysis.
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation | [6 empty] | 0 |  | +2
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements. Increase in line with change of scenario bed space numbers therefore excluded from the analysis.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 -12 | The mix of bays and consult rooms will be dependent on project requirements. One room to be attached or adjacent to a WC for Obstetrics/ Gynaecology patients. Decrease in line with ERG recommendation and benchmarking with recently delivered facilities.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12 spaces scenario
| Consult - Dental | [6 empty] | 12(o) -12 |  | 12(o) -12 | Determined by need/activity. A knee break chair might be included to increase flexibility. Deletion of room in line with ERG recommendation and benchmarking with recently delivered facilities.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  |  |  | 0 |  | -12 |  | -24
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area. Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as although they are highly desirable, it is not always possible to provide in projects.
| Sub-Total Variation | [6 empty] | 0 |  | 0
SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 3 | 3 +3 | Distributed in close proximity from clinical areas. Increase in line with ERG recommendation for better distributed locations within a larger clinical zone and potential multiple pods but final qty dependent on overall staff numbers and ED layout.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | +3
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements. Increase for 8 Bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8 | Optional for 8 bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | 0
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as inclusion is dependent on operational policies.
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as inclusion is dependent on operational policies.
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
| Sub-Total Variation | [8 empty] | 0
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation. Excluded from analysis as provision is dependent on location of ED in relation to hospital staff facilities.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 -5 | 1 | 3 -5 | 1 | 3 -5 | Decrease in line with the change in work practices to reduce paper requirements.
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
| Sub-Total Variation |  |  | 0 |  | -5 |  | -5 |  | -5
| Total Variation |  |  | +9 |  | -5 |  | -16 |  | +13

## ED SOA Comparison_V3 (hidden)
ENTRY / PUBLIC AMENITIES
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Offset doors. Consider trolley & large wheelchair access. Increase in line with previously endorsed Standard Component therefore excluded from analysis.
WAIT-30 | Waiting | Yes | Shared |  | 1 | 25 | 1 | 35 | 1 | 50 | Open, dedicated waiting area observed from Triage & Reception. Area recommendations are indicative and will depend on the approach to sub-wait areas and consideration of local demographics. 1.2m2 recommended per seat, 1.5m2 per wheelchair space. A separated paediatric waiting area is required and may be collocated with the paediatric zone where provided.
PAR | Parenting Room | Yes | Shared |  | 1 | 9 (o) | 1 | 9 | 1 | 9 | Accessible from waiting areas. Increase in line with previously endorsed Standard Component therefore excluded from analysis.
| Bay - Taxi Telephone |  | Shared |  | 1 | 2 (o) | 1 | 2(o) | 1 | 2 (o) | Optional.
| Phone Charging Locker / Kiosk |  | Shared |  | 1 | 1 (o) | 1 | 1 (o) | 1 | 1 (o) | Optional. Optional inclusion in line with benchmarking with recently delivered facilities. Excluded from analysis as inclusion is on project-by-project basis.
BVM | Bay - Vending Machines | Yes | Shared |  | 1 | 2 (o) | 1 | 2 | 2 | 2 | Decrease in line with previously endorsed Standard Component therefore excluded from analysis.
BWTR | Bay - Water | Yes | Shared |  | 1 | 1 | 1 | 1 | 1 | 1
WCPU | Toilet - Public | Yes | Shared |  | 2 | 3 | 3 | 3 | 4 | 3 | Allocation dependent on nearby amenities.
WCAC | Toilet - Accessible | Yes | Shared |  | 1 | 6 (o) | 1 | 6 | 1 | 6
| Changing Places Toilet |  | Shared |  | 1 | 12 (o) | 1 | 12 (o) | 1 | 12 (o) | Optional. Provide if not provided at hospital public amenities. Location to allow shared use between waiting area and clinical zone if provided in ED. Added in line with DDA compliance. Excluded from analysis as provision is dependent on location of ED in relation to main hospital facilities.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | 0
TRIAGE / REGISTRATION
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
REC-E | Reception, Emergency | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Staff to be able to observe & control access to treatment areas. Area allocation will be dependent on number of nursing and clerical staff to be accommodated. 15m2 for 2 staff, 20m2 for 3 staff & 30m2 for 5 staff. May be separate for adult & paediatrics.
TRIAGE-1 TRIAGE-2 | Triage Assessment Room, Emergency |  | Shared |  | 2 | 13 | 3 | 13 | 5 | 13 +26 | No. dependent on operational arrangements. May be provided instead of/or in combination with Triage Desks depending on triage model. Increase in 18 & 36 bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis. Increase in 60 bay scenario in line with ERG recommendation to improve forward movement of patients from waiting room into ED based on their experience with overcrowding in the waiting areas.
| Triage Assessment Desk / Counter |  | Shared |  |  | 6.5 (o) |  | 6.5 (o) |  | 6.5 (o) | Optional. May be provided instead of/or in combination with Triage Rooms depending on triage model. Optional inclusion in line with ERG recommendation and benchmarking with some recently delivered facilities. Excluded from analysis as provision is dependent on models of care and operational model.
| Bay - Fridge |  | Shared |  | Shared | 1 | 1 | 1 +1 | 1 | 1 +1 | Shared by all Triage spaces. Separate fridge for medications and drinks e.g. hydration fluids to support waiting room medicine. Room added in line with benchmarking with recently built facilities.
BHW | Bay - Weight | Yes | Shared |  | 1 | 2 | 1 | 2 | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 6 | 1 | 9 | 1 | 12 | Wheelchair/trolley hold & linen
OFF-1P-9 | Office - Single Person | Yes |  |  |  | 9 |  | 9 |  | 9 | NUM/Front of House coordinator/ local indigenous or cultural representative. Requirements will depend on staff profile and local jurisdictional policies.
| Gun Safe |  | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | 1 | 1(o) | Optional. To be located in a non- public area.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  |  |  | 0 |  | +1 |  | +27
AMBULANCE AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Shower - Decontamination | Yes | 1 | 8 | 1 | 8 | 1 | 8 | 1 | 8 | Check local authority requirements for wastewater detention requirements.
AIRLE-12 | Airlock | Yes | Shared |  | 1 | 12 | 1 | 12 | 1 | 12 | Ambulance entry
PBAT | Patient Bay, Emergency - Ambulance Triage | Yes |  |  | 2 | 6.5 | 3 | 6.5 | 6 | 6.5 | No. dependent on operational arrangements and peak ambulance offloads per hour. Access to patient toilets, dirty utility room and clean/dirty linen required.
| Ambulance Write Up |  |  |  | 1 | 3 | 1 | 5 | 1 | 10 +2 | Ambulance service write up. 2 write up spaces within 5m2. Final spaces dependent on peak number of ambulance officers. Increase in line with recommendation from Ambulance Focus Group to provide adequate space for ambulance officers.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 1 | 1 | 2 | 1 | 1 basin per 4 holding bays.
BBEV | Bay - Beverage, Open Plan | Yes |  |  | Shared |  | Shared |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  | Shared |  | Shared |  | 1 | 2 | For return of ambulance equipment.
| Discounted Circulation |  | 30% |  | 30% |  | 30% |  | 30%
| Sub-Total Variation |  |  | 0 |  | 0 |  | 0 |  | +2
TREATMENT AREAS - RESUSCITATION
AusHFG Room Code | Room / Space | SC / SC-D | 1 Treatment bay |  | 2 Resus Bay |  | 3 Resus Bays |  | 5 Resus Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-R | Patient Bay, Emergency - Resuscitation | Yes |  |  | 2 | 25 | 3 | 25 | 4 | 25 | Number of resuscitation bays is indicative and dependent on clinical services planning. Increase in 2 Resus Bay scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-R | Patient Bay, Emergency - Resuscitation Trauma | Yes | [6 empty] | 1 | 30 | Larger sized resuscitation bay for designated trauma services.
| Patient Bay, Emergency - Treatment / Resuscitation |  | 1 | 25 +9 | [6 empty] | Pendant and other major medical equipment inclusions will be on a project-by-project basis. Increase in line with ACEM, ECI and ERG recommendation to provide a more functional resuscitation space in smaller ED as the room require the same number of staff during resus. The room is also often used as ICU space if patient transfer to a larger facility is delayed.
BMEQ | Bay - Mobile Equipment | Yes | Shared |  | 1 | 4 | 2 | 4 | 3 | 4 | Ultrasound, General X-Ray, other mobile equipment.
OFF-WI-5 | Office - Write Up | [5 empty] | 1 | 3 | 1 | 5
MED-14 | Medication Room | Yes | Shared |  | Shared |  | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes | Shared |  | Shared |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
DTUR-10 | Dirty Utility | Yes | Shared |  | Shared |  | Shared |  | 1 | 10 (o) | Optional. Consider opportunities to share with adjacent zone.
BPATH | Bay - Pathology | Yes | Shared |  | Shared |  | Shared |  | 1 | 2 | For POCT
INTF | Interview Room | Yes | 1 | 12 (o) | 1 | 12 | 1 | 12 | 2 | 12 | Optional for 1 Resuscitation scenario. For staff to meet with family and friends of patients. Also used as a quiet/grieving space. Number will depend on size of service. Also refer to allocation in acute zone below. A larger family or whānau room may also be provided in this zone.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  | +9 |  | 0 |  | 0 |  | 0
TREATMENT AREAS - ACUTE
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Adults + Paeds) |  | 12 Acute Bays (Adults + Paeds) |  | 18 Adult Acute Bays |  | 30 Adult Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes | 6 | 12 | 10 | 12 | 14 | 12 | 24 | 12 -12 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided. Increase for 6, 12 & 18 Bays scenarios in line with change of scenario bed space numbers therefore excluded from the analysis. Decrease for 30 Bays scenarios in line with ERG recommendation of providing more negative pressure bed rooms. Final qty provision dependent on models of care therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | Yes |  |  | 2 | 15 | 2 | 15 | 3 | 15 | May be a mix of adult and paediatric bays where a dedicated paediatric zone is not provided.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class N Isolation | Yes |  |  |  |  | 1 | 15 | 2 | 15 +15 | Negative pressure isolation. Final qty dependent on models of care and provision of an ED pod that can be switched from neutral to negative airflow during pandemic. Increase for 30 Bays scenarios in line with ERG recommendation of providing more negative pressure bed rooms to better manage patients with airborne infections. Benchmarking also showed higher number of negative rooms in larger EDs.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [5 empty] | 15 (o) |  | 15 (o) | Optional. Positive pressure isolation. Inclusion dependent on service provision. Provision is recommended only in specialised ED and dependent on models of care and ED services provision therefore excluded from the analysis.
| Patient Bay, Emergency - Acute Treatment, Bariatric | [5 empty] | 1 | 15 | 1 | 15 | Number dependent on local requirements.
| Obstetrics & Gynaecology Room | [5 empty] | 1 | 14 +14 | 1 | 14 +14 | May be used for sexual assault examination in non-designated site. May also be located in Fast Track depending on models of care. Increase in line with ERG recommendation that this room provision is recommended in new EDs.
ENS-ST-C | Ensuite | [5 empty] | 1 | 5 +5 | 1 | 5 +5 | Attached or adjacent to Obstetrics & Gynaecology Room. Increase in line with ERG recommendation that ensuite provision is provided dedicated to Obstetrics & Gynaecology Room.
ANRM | Anteroom | Yes |  |  |  |  | 1 | 6 | 2 | 6 +6 | Dedicated to each Class N Room Increase for 30 Bays scenarios in line with provision of more negative pressure bed rooms.
ENS-ST-C | Ensuite | Yes |  |  | 2 | 5 | 3 | 5 | 5 | 5 +5 | Dedicated to each Class N, P and Class S room. Increase for 30 Bays scenarios in line with provision of more negative pressure bed rooms.
ENS-BA | Ensuite - Bariatric | Yes |  |  |  |  | 1 | 7 | 1 | 7 | Collocated with bariatric room
| Safe Assessment / Behavioural Assessment Room |  |  |  | 1 | 16 | 1 | 16 | 1 | 16 | For patients presenting with acute, severe behavioural disturbance where clinically indicated. Provision and location will depend on jurisdictional policies.
CONS | Consult Room - Sexual Assault | Yes | [6 empty] | 1 | 12 (o) | Dedicated room required where ED is a designated sexual assault examination site.
ENS-ST-C | Ensuite | Yes | [6 empty] | 1 | 5 (o) | Attached to the Consult Room - Sexual Assault
PROC-20 | Procedure Room | Yes | [6 empty] | 1 | 20 (o) | Included under paediatric zone below for smaller services.
INTF | Interview Room | Yes |  |  | Shared |  | 1 | 12 | 1 | 12 | Number will depend on size of service. Also refer to allocation under resuscitation zone above.
WCPT | Toilet - Patient | Yes | 1 | 4 (o) | 2 | 4 | 2 | 4 | 3 | 4 -4 | Optional for 6 bay scenario depending on location of nearby patient amenities. Increase for 6 bay scenario to show optional WC where no other WC is provided nearby therefore not included in analysis. Decrease for 60 bays scenario in line with ERG recommendation to improve accessibility for large number of patients (swapped for accessible WC).
WCAC | Toilet - Accessible | Yes | 1 | 6 | 1 | 6 | 1 | 6 | 2 | 6 +6 | Increase for 60 bays scenario in line with ERG recommendation to improve accessibility for large number of patients.
SHPT | Shower - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4 -8 | Consider provision of procedural shower in specialised facilities e.g. for burns trauma. Decrease in line with ERG recommendation (as Showers not used often) and benchmarking with recently delivered facilities.
SHAC | Shower - Accessible | Yes | 1 | 4 | 1 | 4 | 1 | 4 | 1 | 4
SSTN-14 | Staff Station | Yes | 1 | 10 | 1 | 14 | 1 | 20 | 1 | 30
| Staff Station, Emergency Control | [5 empty] | 1 | 14 (o) | 1 | 14 (o) | Optional. Provide where Doctor in Charge, Nurse in Charge and Clerk are to be collocated and centralised within the unit to oversee patient flow, ambulance arrival, BAT phone, security feed observation, and central monitoring overview. These functions may be distributed/duplicated across the unit depending on models of operation, staffing profile, size and complexity of service, etc. Optional inclusion in line with ERG recommendation and benchmarking with some recently delivered facilities. Excluded from analysis as provision is dependent on models of care and ED local/regional responsibilities.
OFF-CLN | Office - Clinical Workroom | Yes |  |  |  |  | 1 | 15 | 1 | 20 | To support access to clinical information systems, staff debriefing etc.
MED-14 | Medication Room | Yes | Shared |  | 1 | 8 | 1 | 12 | 2 | 12 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes | Shared |  | 1 | 6 | 1 | 8 | 2 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
BHWS-B | Bay - Handwashing, Type B | Yes | 2 | 1 | 2 | 1 | 3 | 1 | 7 | 1 | 1 basin per 4 treatment bays
| Bay - PPE |  |  | 1 |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BPTS | Bay - Pneumatic Tube | Yes |  |  | 1 | 1 | 1 | 1 | 1 | 1
BPATH | Bay - Pathology | Yes | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | For POCT. Size dependent on no. of devices used.
BRES | Bay - Resuscitation Trolley | Yes | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 2 | 1.5
BMEQ | Bay - Mobile Equipment | Yes | 1 | 4 | 1 | 4 | 2 | 4 | 3 | 4 | Note also allocated under resus and fast track zones. May be provided as underbench storage with staff station.
BLIN | Bay - Linen | Yes | Shared |  | 1 | 2 | 1 | 2 | 2 | 2 | Also included under paediatric and fast track zones.
BBEV | Bay - Beverage, Open Plan | Yes | Shared |  | 1 | 4 | 1 | 4 | 1 | 4
DTUR-10 | Dirty Utility | Yes | Shared |  | 1 | 10 | 1 | 10 | 2 | 10 | No. dependent on size and configuration of ED.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  | 0 |  | 0 |  | +19 |  | +27
PAEDIATRIC ZONE
AusHFG Room Code | Room / Space | SC / SC-D | Paeds bays included above |  | Paeds bays included above |  | 6 Paediatric Acute Bays |  | 12 Paediatric Acute Bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Waiting - Sub | Yes |  |  |  |  | 1 | 10 (o) | 1 | 15 (o) | Optional, where separate paediatric zone provided.
PLAP-10 | Play Area - Paediatric | Yes |  |  |  |  | 1 | 5 (o) | 1 | 10 (o) | Optional. Collocated with paediatric zone where provided.
PBTR-A | Patient Bay, Emergency - Acute Treatment | Yes |  |  |  |  | 4 | 12 | 8 | 12 | Decrease for 12 Bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Acute Treatment, Special | Yes |  |  |  |  | 2 | 15 | 3 | 15
PBTR-AS | Patient Bay, Emergency - Acute Treatment, Special, Class N Isolation | Yes | [6 empty] | 1 | 15 | Negative pressure isolation.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special, Class P Isolation | Yes | [7 empty] | 15 (o) | Optional. Positive pressure isolation. Provision dependent on service provision e.g. trauma burns. Optional inclusion in line with ERG recommendation. Excluded from analysis as provision is dependent on models of care and ED service provision.
ANRM | Anteroom | Yes | [6 empty] | 1 | 6 | Dedicated to each Class N Room
ENS-ST-C | Ensuite - Standard | Yes |  |  |  |  | 2 | 5 | 4 | 5 | Dedicated to each Class N, P and Class S room
PROC-20 | Procedure Room | Yes |  |  |  |  | 1 | 20 | 1 | 20
INTF | Interview Room | [5 empty] | Share |  | 1 | 12
WCPT | Toilet - Patient | Yes | [6 empty] | 1 | 4 -4 | Decrease in line with ERG recommendation to improve accessibility for large number of patients (swapped for accessible WC).
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 +6 | Increase for 12 bays scenario in line with ERG recommendation to improve accessibility for large number of patients.
SHPT | Shower - Patient | Yes | [6 empty] | 1 | 4 | Decrease in line with ERG recommendation to improve accessibility for patients (swapped for accessible shower which is same size) therefore change not included in analysis.
SHAC | Shower - Accessible | Yes |  |  |  |  | 1 | 4 | 1 | 4 | Increase in line with ERG recommendation to improve accessibility for patients(swapped for standard shower which is same size) therefore change not included in analysis.
SSTN-10 | Staff Station | Yes |  |  |  |  | 1 | 10 | 1 | 12
MED-14 | Medication Room | Yes |  |  |  |  | 1 | 6 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes |  |  |  |  | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
BHWS-B | Bay - Handwashing, Type B | Yes |  |  |  |  | 1 | 1 | 3 | 1 | 1 basin per 4 treatment bays
| Bay - PPE | [6 empty] | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BLIN | Bay - Linen | Yes |  |  |  |  | Share |  | 1 | 2
BMEQ | Bay - Mobile Equipment | Yes |  |  |  |  | 1 | 2 | 1 | 4
BBEV | Bay - Beverage, Open Plan | Yes |  |  |  |  | 1 | 4 | 1 | 4
DTUR-S | Dirty Utility - Sub | Yes |  |  |  |  | 1 | 8 | 1 | 8 | No. dependent on size and configuration of ED
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation | [6 empty] | 0 |  | +2
TREATMENT AREAS - FAST TRACK
AusHFG Room Code | Room / Space | SC / SC-D |  |  | 6 Fast Track Spaces |  | 12 Fast Track Spaces |  | 18 Fast Track Spaces |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
WAIT-SUB | Sub-Wait | Yes |  |  |  |  | 1 | 10 | 1 | 15
PBTR-FT | Patient Bay, Emergency - Fast Track | Yes |  |  | 4 | 6.5 | 9 | 6.5 | 14 | 6.5 | The mix of bays and consult rooms will be dependent on project requirements. Increase in line with change of scenario bed space numbers therefore excluded from the analysis.
CONS | Consult Room | Yes |  |  | 2 | 12 | 3 | 12 | 4 | 12 -12 | The mix of bays and consult rooms will be dependent on project requirements. Decrease in line with ERG recommendation and benchmarking with recently delivered facilities.
CONS-ENT-OP | Consult - ENT/ Ophthalmology | Yes |  |  |  |  | 1 | 16 (o) | 1 | 16 | Optional for 12 spaces scenario
| Consult - Dental | [6 empty] | 12(o) -12 |  | 12(o) -12 | Determined by need/activity. A knee break chair might be included to increase flexibility. Deletion of room in line with ERG recommendation and benchmarking with recently delivered facilities.
SSTN-10 | Staff Station | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with an adjacent treatment area.
PLST | Plaster Room | Yes |  |  |  |  | 1 | 14 (o) | 1 | 14 (o) | Optional
| Store - Orthotics and Mobility Aids | [5 empty] | 1 | 2 | 1 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 1 | 1 | 2 | 1 | 3 | 1 | No. dependent on no. patient bays.
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
BRES | Bay - Resuscitation Trolley | Yes |  |  | Shared |  | Shared |  | 1 | 1.5
BMEQ | Bay - Mobile Equipment | Yes |  |  | 1 | 4 | 1 | 4 | 1 | 4
BLIN | Bay - Linen | Yes |  |  | Shared |  | 1 | 2 | 1 | 2
WCPT | Toilet - Patient | Yes |  |  |  |  | 1 | 4 | 2 | 4
WCAC | Toilet - Patient, Accessible | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6
| Discounted Circulation |  |  |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  |  |  | 0 |  | -12 |  | -24
OUTDOOR AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Outdoor Space | [5 empty] | 1 | 20 (o) | 1 | 40 (o) | Optional. Highly desirable in ED with large footprint. Weather protected to part of the area. Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as although they are highly desirable, it is not always possible to provide in projects.
| Sub-Total Variation | [6 empty] | 0 |  | 0
SUPPORT AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays (Acute + Fast Track) |  | 18 bays (Acute + Fast Track) |  | 36 bays (Acute + Fast Track) |  | 60 bays (Acute + Fast Track) |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Office - Telemedicine | [5 empty] | 1 | 12 (o) | 1 | 12 (o) | Optional. Requirement depends on role of facility.
STGN | Store - General | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
STEQ-14 STEQ-20 | Store - Equipment | Yes | Shared |  | 1 | 14 | 1 | 20 | 1 | 30 | May be decentralised for larger EDs. Determine amount of storage required per ED zone and allocate appropriately to that area.
| Store - Disaster Equipment | [7 empty] | 1 | 8 | Requirements will depend on disaster management role.
DISP-10 | Disposal Room | Yes | Shared |  | 1 | 8 | 1 | 10 | 1 | 12 | Area requirement will depend on size of service. Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes.
CLRM | Cleaner's Room | Yes | Shared |  | 1 | 5 | 1 | 5 | 2 | 5 | Number will depend on size of unit.
WCST | Toilet - Staff | Yes | Shared |  | Shared |  | 2 | 3 | 3 | 3 +3 | Distributed in close proximity from clinical areas. Increase in line with ERG recommendation for better distributed locations within a larger clinical zone and potential multiple pods but final qty dependent on overall staff numbers and ED layout.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 45%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | +3
SHORT STAY UNIT
AusHFG Room Code | Room / Space | SC / SC-D | TBC |  | 8 bays |  | 12 bays |  | 20 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | Yes |  |  | 8 | 10 | 11 | 10 | 18 | 10 | Refer to local jurisdictional requirements. Increase for 8 Bays scenario in line with change of scenario bed space numbers therefore excluded from the analysis.
PBTR-AS | Patient Room, Emergency - Non Acute Treatment Special | Yes |  |  |  |  | 1 | 15 | 2 | 15 | Standard isolation
ENS-ST-C | Ensuite | Yes |  |  | 1 | 5 | 3 | 5 | 5 | 5 | Attached to S class isolation rooms and remainder shared between other bays.
ENS-ACC | Ensuite - Accessible |  |  |  | 1 | 7 | 1 | 7 | 1 | 7
SSTN-10 SSTN-20 | Staff Station | Yes |  |  | 1 | 10 | 1 | 12 | 1 | 20
BLIN | Bay - Linen | Yes |  |  | 1 | 2 | 1 | 2 | 2 | 2
BHWS-B | Bay - Handwashing, Type B | Yes |  |  | 2 | 1 | 3 | 1 | 5 | 1 | No. dependent on no. patient bays
| Bay - PPE |  |  |  |  | 1 |  | 1 |  | 1 | Recessed wall mounted PPE holders may be provided instead, depending on IPC policy of the facility. PPE Bay/wall mounted holders must be located to minimise impact on corridor flow.
MED-14 | Medication Room | Yes |  |  | 1 | 6 | 1 | 8 | 1 | 8 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
CLN-10 | Clean Store | Yes |  |  | 1 | 6 | 1 | 6 | 1 | 6 | May be provided as a combined Clean Store / Medication Room depending on local jurisdictional policies. Excluded from the analysis given this change has previously been approved to align with policy requirements for a number of jurisdictions.
DTUR-S | Dirty Utility - Sub | Yes |  |  | 1 | 8 (o) | 1 | 8 | 1 | 8 | Optional for 8 bay scenario.
BRES | Bay - Resuscitation Trolley | Yes |  |  | 1 | 1.5 | 1 | 1.5 | 1 | 1.5
CLRM | Cleaner's Room | Yes |  |  | Shared |  | Shared |  | 1 | 5 | May be shared with acute care zone depending on size of unit.
BBEV | Bay – Beverage, Open Plan | Yes |  |  | Shared |  | 1 | 4 | 1 | 4
BMT | Bay - Meal Trolley | Yes |  |  | Shared |  | 1 | 4 | 1 | 4 | Inclusion dependent on operational policy
STEQ-14 | Store - Equipment | Yes |  |  | Shared |  | 1 | 10 | 1 | 12 | May be shared with acute care zone depending on size of unit.
| Discounted Circulation |  | 40% |  | 40% |  | 40% |  | 40%
| Sub-Total Variation |  |  |  |  | 0 |  | 0 |  | 0
EDUCATION AREAS (OPTIONAL)
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
| Simulation Room | [7 empty] | 1 | 25 (o) | Optional Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as inclusion is dependent on operational policies.
| Simulation Control Room | [7 empty] | 1 | 10 (o) | Optional Optional inclusion in line with ERG recommendation and benchmarking with recently delivered facilities. Excluded from analysis as inclusion is dependent on operational policies.
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
| Sub-Total Variation | [8 empty] | 0
STAFF AREAS
AusHFG Room Code | Room / Space | SC / SC-D | 6 bays |  | 18 bays |  | 36 bays |  | 60 bays |  | Remarks
|  |  | Qty | m2 | Qty | m2 | Qty | m2 | Qty | m2
SRM-15 SRM-35 | Staff Room | Yes | Shared |  | 1 | 15 | 1 | 20 | 1 | 30 | Area dependent on staff profile.
CHST-10 CHST-35 | Change - Staff | Yes | Shared |  | 1 | 10 | 1 | 20 | 1 | 35 | Includes staff toilets and showers. Requirements will depend on operational policy relating to staff arriving at work in uniform or changing at work. Distribution of male, female and non-gendered amenities on project level.
WCAC | Toilet - Accessible | Yes |  |  |  |  | 1 | 6 | 1 | 6 | Unless readily available elsewhere.
PAR | Parenting Room | Yes | Shared |  | Shared |  | 1 | 9 (o) | 1 | 9 (o) | Optional. Dependent on staff profile and location of ED in relation to hospital staff facilities for breastfeeding and lactation. Excluded from analysis as provision is dependent on location of ED in relation to hospital staff facilities.
BPROP | Property Bay - Staff | Yes | Shared |  | 1 | 3 | 1 | 5 | 1 | 8
OFF-1P-12 | Office - Single Person | Yes |  |  |  |  | 1 | 12 | 1 | 12 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-1P-9 | Office - Single Person | Yes |  | 9 |  | 9 |  | 9 |  | 9 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 5.5 |  | 5.5 |  | 5.5 |  | 5.5 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
OFF-WS | Office - Workstation | Yes |  | 4.4 |  | 4.4 |  | 4.4 |  | 4.4 | Allocation will be dependent on staff profile and jurisdictional policies relating to staff work areas.
BMFD-3 | Bay - Multifunction Device, 3m2 | Yes | Shared |  | 1 | 3 -5 | 1 | 3 -5 | 1 | 3 -5 | Decrease in line with the change in work practices to reduce paper requirements.
MEET-20 MEET-30 | Meeting Room | Yes | Shared |  | 1 | 20 | 1 | 30 | 1 | 40 | Consider operable wall to provide as two smaller rooms for higher utilisation.
MEET-15 | Meeting Room | Yes | Shared |  |  |  | 1 | 12 | 1 | 15
| Discounted Circulation |  | 25% |  | 25% |  | 25% |  | 25%
| Sub-Total Variation |  |  | 0 |  | -5 |  | -5 |  | -5
| Total Variation |  |  | 9 |  | -5 |  | +3 |  | +32